## Introduction
Introduction
This Excel document shows calculations for heat reuse scenarios.
Large offtakers in the F&B sector often operate at approximately 8 MW.
Hence, that range is what these figures are adapted to.
It should be noted that there is a major scaling factor in heat reuse, for piping, but also for offtaker's configuration and OPEX costs.
In other words, should even bigger offtaker needs be identified, then that would decrease costs per MW.
Also note that power costs vary substantially, so they need to be checked when estimating true project costs.
For the identified use cases, the figures used are found in the table below. Greyed out cells are not used in the calculations.
On the next tab, those numbers are used for the calculations, and a dropdown menu (at cell H1) automatically inserts the values from the tables.
The third tab shows the estimated gains for the DC heat exchange room.
The costs and gains are made up of avoided infrastructure, new needed infrastructure, fuel cost avoidance, and governmental incentives.
The client pointed out that in many cases, there is already cooling infrastructure in place, so in those cases, "avoidance" would be zero.
Hence, the tab is of relevance both to exisiting and planned DC facilities.
The last tab hosts the system flow diagrams of the scenarios.
This document accompanies the BCA report written simultaneously. To understand the different offtaker cases, HX room configuration, and schamtics, that report should be studied.
Note that manual changes to the populated values in the dropdown list will invalidate future dropdown changes (otherwise a VBA macro would be needed, which may conflict with safety protocol).
So, please make a copy of this file to experiment with the figures, or re-insert them manually after changes, from the table below.
Also, if you are in possession of more case-relevant figures for energy prices, then use them, as they greatly affect the payback period.
Petter Terenius for DGA, August 2025
Location | F&B Facility Type | Distance (m) | 1 MWh Electricity (€) |  | 1 MWh Natural gas (€) |  | Carbon Tax per MWh (€) | Carbon Tax/Subsidy Comment | Total Carbon Cost | CAPEX Subsidies / Green Financing | CAPEX Subsidies / Green Financing Comment | OPEX subsidy / ton avoided carbon (€) | OPEX subsidy… Comment | DC Temp (°C) | Offtaker Temp (°C) | Heat need Total / Heat need DC (MW) | Payback period comment
European average | F&B industry | 1000 | 150 | Electricity prices vary widely: must be investigated by actual case. | 54 | Cheaper per MWh, but carbon taxes and volatility make it less attractive. | 12 | EU ETS only applies to industries over 20 MW; thus it does not pertain to the use cases. | 66 | 30% | CAPEX subsidies are often generous, especially for replacing fossil systems w/ heat pumps. |  | OPEX support is not formalized. EU ETS does not apply. | 30 | 80 | 8.0/5.6
Germany (Frankfurt) | Meat processing | 1560 | 50 | 180 according to Eurostat, but a scheme is currently running (for five years only) | 58 | Prices in this column (excl UK) are from Eurostat, autumn 2024 | 13 | Prices in this column (excl UK) are from Eurostat, autumn 2024 | 71 | 2% | Max 21,000 euros per heat pump. | 0 |  | 30 | 80 | 8.0/5.6
UK/England (Newport) | Processed food | 15000 | 140 | As opposed to typical 215; classified as energy-intensive industries (EII) | 78 |  | 0 | Carbon tax applies mainly to electricity generators | 78 | 0.3% | Limited. There is a £7,500 guaranteed grant per heat pump. | 0 | Other scheme: Climate Change Agreements (CCA) | 55 (mix) | 55 | 8.0/5.6
The Netherlands (Agriport A7) | Horticulture | 1000 | 100 | As opposed to Eurostat's 117, for large industries | 42 |  | 20 |  | 62 | 30% | ISDE subsidy. | 0 |  | 55 | 55 | 8.0/5.6 | Proposed solution does not need heat pumps. The calculation is not supported properly.
Spain (Zaragoza) | Beer | 3000 | 90 | As opposed to Eurostat's 98, for large industries | 48 |  | 4 |  | 52 | 50% | Funded via IDAE. Here: 35% for heat pump and another 15% for installation. | 0 | More schemes: The Interruptibility program; The Capacity market program | 30 | 80 | 8.0/5.6
Sweden (Staffanstorp) | Oat milk production | 30000 | 90 | In Sweden’s SE4 bidding zone. Reasonable for a large industry (100 in Eurostat) | 78 |  | 31 |  | 109 | 25% | No fixed amount. Swedish Energy Agency grants, EU funding mechanisms | 0 |  | 30 | 75 | 8.0/5.6 | Sweden has no gas-powered industries, so the calculation is not supported properly.
Natural gas costs are based on many sources, including:
https://tradingeconomics.com/commodity/eu-natural-gas
https://www.iea.org/reports/gas-market-report-q3-2025/executive-summary
https://ec.europa.eu/eurostat/statistics-explained/images/d/d6/Statistic_Explained_figures_for_Gas_2024S2_v2.xlsx

## Offtaker and Piping
|  |  |  | European average |  |  | Click yellow field to view dropdown list
Offtaker System and Piping
The system on this tab excludes DC costs (infrastructure) and savings (cooling) |  |  |  | Distance (m) DC to Offtaker |  | 1000 | [6 empty] | This is NOT used in the calculation; just included for reference
Delta-T is 12°C on the DC side. |  |  |  | Distance in feet |  | 3281 | Note that changes to the values below
Offtaker power need is 8 MW. Power from DC is 5.6 MW. | [6 empty] | will invalidate further dropdown changes. | [5 empty] | Temperature Loss Over Distance
Assumes 8760 hour operation. |  |  |  | Electricity price per MWh (€) |  | 150 | [6 empty] | Outgoing water temperature (30°C) from DC |  | 30
|  |  |  | Natural gas price per MWh (€) |  | 54 | [6 empty] | Ambient temperature (typically 6-10 °C) |  | 6
Petter Terenius for DGA, July-August 2025 |  |  |  | Carbon tax per MWh (€) |  | 12 | EU ETS only applies to industries over 20 MW; thus it does not pertain to the use cases. | [5 empty] | Heat loss (°C) |  | 0.053543
|  |  |  | CAPEX subsidy (%) |  | 30% | CAPEX subsidies are often generous, especially for replacing fossil systems w/ heat pumps.
|  |  |  | OPEX subsidy per ton avoided c. (€) |  | 0 | OPEX support is not formalized. EU ETS does not apply.
[13 empty] | Remaining heat (°C) |  | 29.9465
30°C (86°F) scenario |  |  |  | 65°C (150°F) scenario
Water leaves DC at 30°C and returns at 18°C |  |  |  | Water leaves DC at 65°C and returns at 53°C
PIPING CAPEX |  |  |  | PIPING CAPEX |  |  |  |  | Comments |  |  | Piping Heat Loss Calculator
Cost Component | Cost/Meter | Estimated Cost (€) |  | Cost Component |  | Cost/Meter | Estimated Cost (€) |  |  |  |  | Water temperature from DC |  | 30
Insulated pipe (forward), 250 mm | 120 | 120000 |  | Insulated pipe (forward), 250 mm |  | 120 | 120000 |  | Insulated HDPE (SDR17) pipe forward; uninsulated same-size HDPE pipe return. Velocity rate: 2.3 m/s. |  |  | Ambient temperature |  | 6 | Likely 6-10 degrees for buried pipe in Europe
Uninsulated pipe (return), 250 mm | 45 | 45000 |  | Uninsulated pipe (return), 250 mm |  | 45 | 45000 |  | Dimensioning is a factor of heat needs, and affects pipe pricing. |  |  | Difference water/ambient temp |  | 24 | Pipe inner diameter D=0.1308 m
Valves, fittings, sensors | 10 | 10000 |  | Valves, fittings, sensors |  | 10 | 10000 |  | Valves, fittings, sensors are €4000 per km |  |  | U value for pipe |  | 0.5 | Insulation value. Varies a lot. U=x W/m²·K | https://www.isoplus.group/products/product-portfolio/details/product/isoflex-single-pipe/
Installation and trenching | 100 | 100000 |  | Installation |  | 100 | 100000 |  | Trenching costs are heavily dependent on terrain and on hindering infrastructure. |  |  | Qloss (W/m) |  | 4.9309 | Qloss = U*pi*D*deltaT
Project management and design | 50 | 50000 |  | Project management and design |  | 50 | 50000
Pumps to keep pressure over distances (€5000/10 km) |  | 5000 |  | Pumps to keep pressure over distances (€5000 /10 km) |  |  | 5000
Distance (m) | 1000 |  |  | Distance (m) |  | 1000 |  |  | Note that at 65°C, steel pipes may be preferable for endurance. This would increase costs by up to 100%. |  |  | Heat loss (°C/m) |  | 5.3543e-05 | Flow rate = 22 kg/s
Total |  | 330000 |  | Total |  |  | 330000 |  |  |  |  | Heat loss for installation (°C) |  | 0.053543 | deltaT = (Qloss)/(flow rate*water specific heat capacity)
[12 empty] | Remaining heat (°C) |  | 29.9465
HEAT PUMP CAPEX per unit |  |  |  | HEAT PUMP CAPEX
Cost Component | % of HP Cost | Estimated Cost (€) |  | Cost Component |  | % of HP Cost | Estimated Cost (€)
8 MW Heat Pump Unit | n/a | 2500000 |  | 8 MW High-Temp Heat Pump Unit |  | n/a | 2500000 |  | Instead of one 8 MW heat pump, it may be advisable to install 2*4 MW heat pumps.
System Integration | 20% | 500000 |  | System Integration |  | 20% | 500000 |  | That would allow for partial load operation and for maintenance without full shutdown.
Automation & Controls | 20% | 500000 |  | Automation & Controls |  | 20% | 500000 |  | The associated CAPEX increasee for that scenario is 10-20%.
Refrigerants | 5% | 125000 |  | Refrigerants |  | 5% | 125000
Installation & Commissioning | 50% | 1250000 |  | Installation & Commissioning |  | 50% | 1250000
Total |  | 4875000 |  | Total |  |  | 4875000
STORAGE TANK CAPEX |  |  |  | STORAGE TANK CAPEX
Cost Component | Notes | Estimated Cost (€) |  | Cost Component |  | % of Tank Cost | Estimated Cost (€)
Tank, 100 m3, plus insulation | Gives 30 mins | 130000 |  | Tank, 100 m3, plus insulation |  | Gives 30 mins | 130000 |  | Needed to level out fluctuations due to differences in returning temperature from offtaker's processes.
Controls, sensors, installation | buffer at full heat | 120000 |  | Controls, sensors, installation |  | buffer at full heat | 120000
Total |  | 250000 |  | Total |  |  | 250000
HEAT EXCHANGER CAPEX |  |  |  | HEAT EXCHANGERS CAPEX
Cost Component | % of HX Cost | Estimated Cost (€) |  | Cost Component |  | % of HX Cost | Estimated Cost (€)
Heat Exchanger Industrial Process |  | 200000 |  | Heat Exchanger Industrial Process |  |  | 200000
Installation | 10% | 20000 |  | Heat Exchanger Fluctuations |  |  | 100000
Total |  | 220000 |  | Installation |  | 10% | 30000
|  |  |  | Total |  |  | 330000
TOTAL SYSTEM CAPEX |  |  |  | TOTAL SYSTEM CAPEX
Cost Component |  | Estimated Cost (€) |  | Cost Component |  |  | Estimated Cost (€)
Piping and Trenching |  | 330000 |  | Piping and Trenching |  |  | 330000
2 Heat Pumps |  | 9750000 |  | Heat Pump |  |  | 4875000
Storage Tank |  | 250000 |  | Storage Tank |  |  | 250000
4 Heat Exchangers (possibly 1 chiller) |  | 880000 |  | 2 Heat Exchangers |  |  | 330000
Total |  | 11210000 |  | Total |  |  | 5785000
PIPING OPEX |  |  |  | PIPING OPEX
Cost Component | Cost / Meter | Estimated Cost (€) |  | Cost Component |  | Cost / Meter | Estimated Cost (€)
Crude estimate | 45 | 45000 |  | Crude estimate |  | 45 | 45000
Distance (m) | 1000 |  |  | Distance (m) |  | 1000
Total |  | 45000 |  | Total |  |  | 45000
HEAT PUMP OPEX both units |  |  |  | HEAT PUMP OPEX
Cost Component | Notes | Estimated Cost (€) |  | Cost Component |  | % of HP Cost | Estimated Cost (€)
Electricity HP A | 1.21 MW added | 1589940 |  | Electricity |  | COP: 7.0 | 1419120
Electricity HP B | 1.49 MW added | 1851426 |  | Maintenance |  | Temp lift: 12°C | 80000 |  | Unusually low temperature lift for 65 degree scenario.
Maintenance |  | 80000 |  | Monitoring & Control |  | 1.08 MW added | 20000 |  | Could be reconfigured in several ways.
Monitoring & Control |  | 20000 |  | Insurance & Admin |  | electricity | 15000
Insurance & Admin |  | 15000 |  | Total |  |  | 1534120
Total |  | 3556366
STORAGE TANK OPEX |  |  |  | STORAGE TANK OPEX
Cost Component |  | Estimated Cost (€) |  | Cost Component |  |  | Estimated Cost (€)
Total OPEX |  | 5000 |  | Total OPEX |  |  | 5000
Total |  | 5000 |  | Total |  |  | 5000
HEAT EXCHANGER OPEX |  |  |  | HEAT EXCHANGER OPEX
Cost Component |  | Estimated Cost (€) |  | Cost Component |  |  | Estimated Cost (€)
Maintenance |  | 10000 |  | Maintenance for both units |  |  | 15000
Total |  | 10000 |  | Total |  |  | 15000
TOTAL SYSTEM OPEX |  |  |  | TOTAL SYSTEM OPEX
Cost Component |  | Estimated Cost (€) |  | Cost Component |  |  | Estimated Cost (€)
Pipe maintenance |  | 45000 |  | Pipe maintenance |  |  | 45000
2 Heat Pumps, electricity and maintenance |  | 3556366 |  | Heat Pump electricity and maintenance |  |  | 1534120
Storage Tank maintenance |  | 5000 |  | Storage Tank maintenance |  |  | 5000
Heat Exchangers electricity and maintenance |  | 10000 |  | Heat Exchanger electricity and maintenance |  |  | 15000
Total |  | 3606366 |  | Total |  |  | 1584120
PROJECT CASHFLOW: 30°C scenario
Undiscounted and without inflation
| Current | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10
OPEX |  | 776743.4451 | 776743.4451 | 776743.4451 | 776743.4451 | 776743.4451 | 776743.4451 | 776743.4451 | 776743.4451 | 776743.4451 | 776743.4451
Piping and Trenching |  | -45000 | -45000 | -45000 | -45000 | -45000 | -45000 | -45000 | -45000 | -45000 | -45000
Heat Pumps maintenance |  | -115000 | -115000 | -115000 | -115000 | -115000 | -115000 | -115000 | -115000 | -115000 | -115000
Storage Tank maintenance |  | -5000 | -5000 | -5000 | -5000 | -5000 | -5000 | -5000 | -5000 | -5000 | -5000
Heat Exchanger maintenance |  | -10000 | -10000 | -10000 | -10000 | -10000 | -10000 | -10000 | -10000 | -10000 | -10000
Electricity for Heat Pumps |  | -3441366 | -3441366 | -3441366 | -3441366 | -3441366 | -3441366 | -3441366 | -3441366 | -3441366 | -3441366
Cost of carbon displaced (1111 kWh per hour and MW) |  | 4204379.52 | 4204379.52 | 4204379.52 | 4204379.52 | 4204379.52 | 4204379.52 | 4204379.52 | 4204379.52 | 4204379.52 | 4204379.52
Avoided carbon tax (MWh CO2/year) |  | 188729.9251 | 188729.9251 | 188729.9251 | 188729.9251 | 188729.9251 | 188729.9251 | 188729.9251 | 188729.9251 | 188729.9251 | 188729.9251
Natural Gas displaced, MWh per year |  | 77858.88 | 77858.88 | 77858.88 | 77858.88 | 77858.88 | 77858.88 | 77858.88 | 77858.88 | 77858.88 | 77858.88
Natural Gas displaced, Tons CO2 per year |  | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938
CAPEX | -10550000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Piping and Trenching | -330000
Heat Pump(s) | -9750000
Storage Tank | -250000
Heat Exchangers | -220000
Subsidy | -3165000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-off subsidy | -3165000
Carbon subsidy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Savings | -7385000 | 776743.4451 | 776743.4451 | 776743.4451 | 776743.4451 | 776743.4451 | 776743.4451 | 776743.4451 | 776743.4451 | 776743.4451 | 776743.4451
Cumulative Impact | -7385000 | -6608256.5549 | -5831513.1098 | -5054769.6646 | -4278026.2195 | -3501282.7744 | -2724539.3293 | -1947795.8842 | -1171052.439 | -394308.9939 | 382434.4512
PAYBACK PERIOD AND OUTLOOK: 30°C scenario
Payback period | 9.5076
System profit after ten years | 382434.4512
PROJECT CASHFLOW: 65°C scenario
Undiscounted and without inflation
| Current | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10
OPEX |  | 2605259.52 | 2605259.52 | 2605259.52 | 2605259.52 | 2605259.52 | 2605259.52 | 2605259.52 | 2605259.52 | 2605259.52 | 2605259.52
Piping and Trenching |  | -45000 | -45000 | -45000 | -45000 | -45000 | -45000 | -45000 | -45000 | -45000 | -45000
Heat Pumps maintenance |  | -115000 | -115000 | -115000 | -115000 | -115000 | -115000 | -115000 | -115000 | -115000 | -115000
Storage Tank maintenance |  | -5000 | -5000 | -5000 | -5000 | -5000 | -5000 | -5000 | -5000 | -5000 | -5000
Heat Exchanger maintenance |  | -15000 | -15000 | -15000 | -15000 | -15000 | -15000 | -15000 | -15000 | -15000 | -15000
Electricity for Heat Pump |  | -1419120 | -1419120 | -1419120 | -1419120 | -1419120 | -1419120 | -1419120 | -1419120 | -1419120 | -1419120
Cost of carbon displaced (1111 kWh per hour and MW) |  | 4204379.52 | 4204379.52 | 4204379.52 | 4204379.52 | 4204379.52 | 4204379.52 | 4204379.52 | 4204379.52 | 4204379.52 | 4204379.52
Avoided carbon tax (Tons CO2/year) |  | 188729.9251 | 188729.9251 | 188729.9251 | 188729.9251 | 188729.9251 | 188729.9251 | 188729.9251 | 188729.9251 | 188729.9251 | 188729.9251
Natural Gas displaced, MWh per year |  | 77858.88 | 77858.88 | 77858.88 | 77858.88 | 77858.88 | 77858.88 | 77858.88 | 77858.88 | 77858.88 | 77858.88
Natural Gas displaced, Tons CO2 per year |  | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938
CAPEX | -5485000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Piping and Trenching | -330000
Heat Pump(s) | -4875000
Storage Tank | -250000
Heat Exchangers | -30000
Subsidy | -1645500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-off subsidy | -1645500
Carbon subsidy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Savings | -3839500 | 2605259.52 | 2605259.52 | 2605259.52 | 2605259.52 | 2605259.52 | 2605259.52 | 2605259.52 | 2605259.52 | 2605259.52 | 2605259.52
Cumulative Impact | -3839500 | -1234240.48 | 1371019.04 | 3976278.56 | 6581538.08 | 9186797.6 | 11792057.12 | 14397316.64 | 17002576.16 | 19607835.68 | 22213095.2
PAYBACK PERIOD AND OUTLOOK: 65°C scenario
Payback period | 1.4737
System profit after ten years | 22213095.2
Note on D155: Petter Terenius: Note that the CO2 avoidance is the same as from the 30 degree scenario; it's just that the temp lift is at the DC side.

## DC Economics
Data Center Economics
HEAT EXCHANGE ROOM CAPEX
Cost Component | Description | Gain/Cost (€)
HEAT REUSE CASE |  | 792000 | Where there is exisiting infrastructure, this is the CAPEX.
Plate heat exchanger | Acts as a thermal bridge, transferring heat between loops | 70000
Primary pumps | Circulate water through the datacenter loop | 40000
Secondary pumps | Circulate water to the recipient loop | 40000
Control valves etc | Regulate flow and temperature | 15000
Temp & flow sensors | Monitor inlet/outlet temperatures and flow rates | 6000
Expansion tank | Manages pressure changes in the closed loop | 8000
Water treatment | Prevents corrosion and scaling in the loop | 10000
Piping | Connects components within the room | 40000
Monitoring system | Controls and monitors system performance | 20000
Safety measures | Racks, mounts, drip trays, leak detection, fire safety | 15000
Redundancy material | 50% of system cost | 132000
Installation etc | 100% of system cost (including redundancy materials) | 396000
HEAT REJECTION CASE | In other words, cost avoidance | 10450000 | Where there will be no need to build heat rejection infrastructure, use this.
Electric chillers (5.3 MW) | High-efficiency chillers | 3000000 | Be careful with the minus sign, though!
Cooling towers | Rejects heat from condenser water loop | 1500000
Chilled water pumps, piping | Circulates chilled water between chillers and air handlers | 700000
Condenser water pumps | Circulates water between chillers and cooling towers | 400000
Control system | Monitoring and optimization | 350000
Backup power system | UPS + batteries or diesel gensets for cooling continuity | 1500000
Installation etc | Labor, integration, testing | 3000000
Total CAPEX savings |  | 9658000 | If no cooling infrastructure exists.
Notes
This calculation shows the difference between cooling and employing heat reuse for 5.6 MW in a data center.
It does not factor in costs which would have been present in both cases, such as air coolers in server rooms.
HEAT EXCHANGE ROOM OPEX COMPARISON
Cost Component | Comment | Gain/Cost (€)
HEAT REUSE CASE |  | 220000
Electricity |  | 120000 | Pumps draw 100 kW.
Maintenance | Simpler components, fewer moving parts | 60000
Chemical treatment |  | 15000
Monitoring system | Less complex automation in reuse system | 25000 | 100000 | Total excl power
HEAT REJECTION CASE | In other words, cost avoidance | 3170000
Electricity | Pumps only in reuse system | 2500000 | Power draw by chillers is approximately 2.0 MW.
Maintenance |  | 300000 | Fans and pumps add another 350 kW.
Water usage | 70,000 m3 per year | 220000 | Power draw diff (MW): | 2.2
Chemical treatment | Cooling towers require more aggressive treatment | 50000
Monitoring system |  | 100000
Total savings excluding power |  | 570000 | 670000 | Total excl power
Total OPEX gain |  | 2950000
Notes
The huge difference in annual operating cost (more than 90% reduction in heat reuse case) mainly stems from power savings.
INCENTIVE LIST
For a 5.6 MW DC heat reuse scenario (8 MW at offtaker including heat pump)
Country | Incentive | Possible savings (€ M)
GERMANY
| CAPEX | 5360000
| Corporate depreciation acceleration | 2240000
| Regional grant programmes (Land-level) | 1120000
| New EU funding (?) | 2000000
| OPEX | 800000
| EU ETS (for a 60 MW+ DC) | 800000
UNITED KINGDOM
| CAPEX | 7840000
| 100 % Enhanced Capital Allowance | 2800000
| Accelerated writing-down on new-build M & E | 1680000
| Green Heat Network Fund grant | 3360000
| OPEX | 800000
| UK ETS (for a 60 MW+ DC) | 800000
NETHERLANDS
| CAPEX | 7940000
| Energy Investment Allowance (EIA) | 2020000
| SDE ++ subsidy for recovered heat | 3920000
| New EU funding (?) | 2000000
| OPEX | 800000
| EU ETS (for a 60 MW+ DC) | 800000
SPAIN
| CAPEX | 4240000
| Capital-allowance uplift (pending) | 2240000
| New EU funding (?) | 2000000
| OPEX | 900000
| VAT reduction on heat sales | 100000
| EU ETS (for a 60 MW+ DC) | 800000
SWEDEN
| CAPEX | 2560000
| Municipal / EU grant rounds | 560000
| New EU funding (?) | 2000000
| OPEX | 800000
| EU ETS (for a 60 MW+ DC) | 800000
TOTAL CAPEX SAVINGS ON DC SIDE
Compared with heat rejection through cooling towers
Cost Component |  | Gain (€)
GERMANY |  | 9895600
Cooling - Heat exchange room |  | 9658000
Incentives estimate, 30% of CAPEX |  | 237600
UNITED KINGDOM |  | 9895600
Cooling - Heat exchange room |  | 9658000
Incentives estimate, 30% of CAPEX |  | 237600
THE NETHERLANDS |  | 9895600
Cooling - Heat exchange room |  | 9658000
Incentives estimate, 30% of CAPEX |  | 237600
SPAIN |  | 9895600
Cooling - Heat exchange room |  | 9658000
Incentives estimate, 30% of CAPEX |  | 237600
SWEDEN |  | 9895600
Cooling - Heat exchange room |  | 9658000
Incentives estimate, 30% of CAPEX |  | 237600
TOTAL OPEX SAVINGS ON DC SIDE
Compared with heat rejection through cooling towers
Cost Component |  | Gain (€)
GERMANY |  | 7140000
Maintenance, treatment, water savings |  | 570000
Power cost gain |  | 963600
OPEX subsidies |  | 5606400 | EU ETS carbon credits give approximately €80 per MWh.
UNITED KINGDOM |  | 8874480
Maintenance, treatment, water savings |  | 570000
Power cost gain |  | 2698080
OPEX subsidies |  | 5606400
THE NETHERLANDS |  | 8103600
Maintenance, treatment, water savings |  | 570000
Power cost gain |  | 1927200
OPEX subsidies |  | 5606400
SPAIN |  | 8010880
Maintenance, treatment, water savings |  | 570000
Power cost gain |  | 1734480
OPEX subsidies |  | 5706400
SWEDEN |  | 7910880
Maintenance, treatment, water savings |  | 570000
Power cost gain |  | 1734480
OPEX subsidies |  | 5606400
PROJECT CASHFLOW: DATA CENTER
Undiscounted and without inflation
|  | Current | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10
OPEX |  |  | 2950000 | 2950000 | 2950000 | 2950000 | 2950000 | 2950000 | 2950000 | 2950000 | 2950000 | 2950000
Heat reuse case |  |  | -220000 | -220000 | -220000 | -220000 | -220000 | -220000 | -220000 | -220000 | -220000 | -220000
Heat rejection case | Savings from not needing on-premise cooling |  | 3170000 | 3170000 | 3170000 | 3170000 | 3170000 | 3170000 | 3170000 | 3170000 | 3170000 | 3170000
Yearly incentive |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CAPEX |  | -792000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat reuse case |  | -792000
(Heat rejection case) | 10450000 | 0
0
Subsidy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-off subsidy |  | 0
Annual subsidies |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Savings |  | -792000 | 2950000 | 2950000 | 2950000 | 2950000 | 2950000 | 2950000 | 2950000 | 2950000 | 2950000 | 2950000
Cumulative Impact |  | -792000 | 2158000 | 5108000 | 8058000 | 11008000 | 13958000 | 16908000 | 19858000 | 22808000 | 25758000 | 28708000
PAYBACK PERIOD AND OUTLOOK
Payback period |  | 0.26847
System profit after ten years |  | 28708000

## System Flow Diagrams
System Flow Diagrams