## Introduction
Introduction
This Excel document shows calculations for offtaker's heat reuse scenarios.
Large offtakers in the F&B sector often operate at approximately 8 MW.
Hence, that range is what these figures are adapted to.
It should be noted that there is a major scaling factor in heat reuse, for piping, but also for offtaker's configuration and OPEX costs.
In other words, should even bigger offtaker needs be identified, then that would decrease costs per MW.
Also note that power costs vary substantially, so they need to be checked when estimating true project costs.
For the identified use cases, the figures used are found in the table below. Greyed out cells are not used in the calculations.
On the next tab, those numbers are used for the calculations, and a dropdown menu automatically inserts the values from the tables.
The third tab hosts the system flow diagrams of the scenarios.
Note that manual changes to the populated values will invalidate future dropdown changes (otherwise a VBA macro would be needed, which may conflict with safety protocol).
So, please make a copy of this file to experiment with the figures, or re-insert them manually after changes, from the table below.
Petter Terenius for DGA, August 2025
Location | F&B Facility Type | Distance (m) | 1 MWh Electricity (€) |  | 1 MWh Natural gas (€) |  | Carbon Tax (€) | Carbon Tax Comment | CAPEX Subsidies / Green Financing | CAPEX Subsidies / Green Financing Comment | OPEX subsidy / ton avoided carbon (€) | OPEX subsidy… Comment | DC Temp (°C) | Offtaker Temp (°C) | Heat need Total / Heat need DC (MW) | Payback period comment
European average | F&B industry | 1000 | 117 | Electricity prices vary widely: must be investigated by actual case. | 32 | Cheaper per MWh, but carbon taxes and volatility make it less attractive. | 57 | In the EU, mainly EU ETS. | 30% | CAPEX subsidies are often generous, especially for replacing fossil systems w/ heat pumps. |  | OPEX support is not formalized. | 30 | 80 | 8.0/5.6
Germany (Frankfurt) | Meat processing | 1560 | 160 |  | 80 |  | 73 | EU ETS | 2% | Max 21,000 euros per heat pump. | 0 | No direct operational subsidy. | 30 | 80 | 8.0/5.6
UK/England (Newport) | Processed food | 15000 | 122 |  | 81 |  | 0 | Carbon tax (22 euros/ton) applies mainly to electricity generators | 0.3% | Limited. There is a £7,500 guaranteed grant per heat pump. | 0 | No direct operational subsidy. | 55 (mix) | 55 | 8.0/5.6
The Netherlands (Agriport A7) | Horticulture | 1000 | 152 |  | 32 |  | 74 | Dutch national CO₂ levy, semi-aligned w/ EU ETS | 30% | ISDE subsidy. | 0 | No direct operational subsidy. | 55 | 55 | 8.0/5.6 | Proposed solution does not need heat pumps. The calculation is not supported properly.
Spain (Zaragoza) | Beer | 3000 | 98 |  | 33 |  | 73 | EU ETS | 50% | Funded via IDAE. Here: 35% for heat pump and another 15% for installation. | 0 | No direct operational subsidy. | 30 | 80 | 8.0/5.6
Sweden (Staffanstorp) | Oat milk production | 30000 | 52 | In Sweden’s SE3 bidding zone | 113 |  | 73 | EU ETS. In principle zero, as gas is not used. | 25% | No fixed amount. Swedish Energy Agency grants, EU funding mechanisms | 0 | No direct operational subsidy. | 30 | 75 | 8.0/5.6 | Sweden has no gas-powered industries, so the calculation is not supported properly.

## Offtaker and Piping
European average
|  |  |  | Payback period, 30°C (if applicable) |  | 32.0669
Offtaker System and Piping
System excludes DC costs (infrastructure) and savings (cooling) |  |  |  | Distance (m) DC to Offtaker |  | 1000 | [6 empty] | This is NOT used in the calculation; just included for reference
Delta-T is 12°C on the DC side. Offtaker power need is 8 MW. |  |  |  | Distance in feet |  | 3281 | Note that changes to the values below
Assumes 8760 hour operation. | [6 empty] | will invalidate further dropdown changes. | [5 empty] | Temperature Loss Over Distance
|  |  |  | Electricity price per MWh (€) |  | 117 | [6 empty] | Outgoing water temperature (30°C) from DC |  | 30
Petter Terenius for DGA, July-August 2025 |  |  |  | Natural gas price per MWh (€) |  | 32 | [6 empty] | Ambient temperature (typically 6-10 °C) |  | 6
|  |  |  | Carbon tax per ton (€) |  | 57 | In the EU, mainly EU ETS. | [5 empty] | Heat loss (°C) |  | 0.053543
|  |  |  | CAPEX subsidy (%) |  | 30% | CAPEX subsidies are often generous, especially for replacing fossil systems w/ heat pumps.
|  |  |  | OPEX subsidy per ton avoided c. (€) |  | 0 | OPEX support is not formalized.
[13 empty] | Remaining heat (°C) |  | 29.9465
30°C (86°F) scenario |  |  |  | 65°C (150°F) scenario
Water leaves DC at 30°C and returns at 18°C |  |  |  | Water leaves DC at 65°C and returns at 53°C
PIPING CAPEX |  |  |  | PIPING CAPEX |  |  |  |  | Comments |  |  | Piping Heat Loss Calculator
Cost Component | Cost/Meter | Estimated Cost (€) |  | Cost Component |  | Cost/Meter | Estimated Cost (€) |  |  |  |  | Water temperature from DC |  | 30
Insulated pipe (forward), 160 mm | 45 | 45000 |  | Insulated pipe (forward), 160 mm |  | 45 | 45000 |  | Insulated HDPE (SDR11) pipe forward; uninsulated same-size HDPE pipe return. Velocity rate: 2.0 m/s. |  |  | Ambient temperature |  | 6 | Likely 6-10 degrees for buried pipe in Europe
Uninsulated pipe (return), 160 mm | 22 | 22000 |  | Uninsulated pipe (return), 160 mm |  | 22 | 22000 |  | Dimensioning is a factor of heat needs, and affects pipe pricing. |  |  | Difference water/ambient temp |  | 24 | Pipe inner diameter D=0.1308 m
Valves, fittings, sensors | 10 | 10000 |  | Valves, fittings, sensors |  | 10 | 10000 |  | Valves, fittings, sensors are €4000 per km |  |  | U value for pipe |  | 0.5 | Insulation value. Varies a lot. U=x W/m²·K | https://www.isoplus.group/products/product-portfolio/details/product/isoflex-single-pipe/
Installation and trenching | 100 | 100000 |  | Installation |  | 100 | 100000 |  | Trenching costs are heavily dependent on terrain and on hindering infratructure. |  |  | Qloss (W/m) |  | 4.9309 | Qloss = U*pi*D*deltaT
Project management and design | 50 | 50000 |  | Project management and design |  | 50 | 50000
Pumps to keep pressure over distances (€5000/10 km) |  | 5000 |  | Pumps to keep pressure over distances (€5000 /10 km) |  |  | 5000
Distance (m) | 1000 |  |  | Distance (m) |  | 1000 |  |  | Note that at 65°C, steel pipes may be preferable for endurance. This would increase costs by up to 100%. |  |  | Heat loss (°C/m) |  | 5.3543e-05 | Flow rate = 22 kg/s
Project management etc |  | 40000 |  | Project management etc |  |  | 40000
Total |  | 272000 |  | Total |  |  | 272000 |  |  |  |  | Heat loss for installation (°C) |  | 0.053543 | deltaT = (Qloss)/(flow rate*water specific heat capacity)
[12 empty] | Remaining heat (°C) |  | 29.9465
HEAT PUMP CAPEX per unit |  |  |  | HEAT PUMP CAPEX
Cost Component | % of HP Cost | Estimated Cost (€) |  | Cost Component |  | % of HP Cost | Estimated Cost (€)
8 MW Heat Pump Unit | n/a | 2200000 |  | 8 MW High-Temp Heat Pump Unit |  | n/a | 2600000 |  | These figures are rather volatile and must be discussed on a case-by-case basis.
System Integration | 20% | 440000 |  | System Integration |  | 20% | 520000 |  | Here, they cost is moderate to high.
Automation & Controls | 20% | 440000 |  | Automation & Controls |  | 20% | 520000 |  | Slightly higher price estimate for the 65 degree heat pump, due to untypically high inlet temperature.
Installation & Commissioning | 40% | 880000 |  | Installation & Commissioning |  | 40% | 1040000
Total |  | 3960000 |  | Total |  |  | 4680000
STORAGE TANK CAPEX |  |  |  | STORAGE TANK CAPEX
Cost Component | Notes | Estimated Cost (€) |  | Cost Component |  | % of Tank Cost | Estimated Cost (€)
Tank, 100 m3, plus insulation | Gives 30 mins | 130000 |  | Tank, 100 m3, plus insulation |  | Gives 30 mins | 130000 |  | Needed to level out fluctuations due to differences in returning temperature from offtaker's processes.
Controls, sensors, installation | buffer at full heat | 120000 |  | Controls, sensors, installation |  | buffer at full heat | 120000
Total |  | 250000 |  | Total |  |  | 250000
HEAT EXCHANGER CAPEX |  |  |  | HEAT EXCHANGERS CAPEX
Cost Component | % of HX Cost | Estimated Cost (€) |  | Cost Component |  | % of HX Cost | Estimated Cost (€)
Heat Exchanger Industrial Process |  | 300000 |  | Heat Exchanger Industrial Process |  |  | 300000
Installation | 10% | 30000 |  | Heat Exchanger Fluctuations |  |  | 100000
Total |  | 330000 |  | Installation |  | 10% | 40000
|  |  |  | Total |  |  | 440000
TOTAL SYSTEM CAPEX |  |  |  | TOTAL SYSTEM CAPEX
Cost Component |  | Estimated Cost (€) |  | Cost Component |  |  | Estimated Cost (€)
Piping and Trenching |  | 272000 |  | Piping and Trenching |  |  | 272000
2 Heat Pumps |  | 7920000 |  | Heat Pump |  |  | 4680000
Storage Tank |  | 250000 |  | Storage Tank |  |  | 250000
Heat Exchanger |  | 330000 |  | 2 Heat Exchangers |  |  | 440000
Total |  | 8772000 |  | Total |  |  | 5642000
PIPING OPEX |  |  |  | PIPING OPEX
Cost Component | Cost / Meter | Estimated Cost (€) |  | Cost Component |  | Cost / Meter | Estimated Cost (€)
Crude estimate | 45 | 45000 |  | Crude estimate |  | 45 | 45000
Distance (m) | 1000 |  |  | Distance (m) |  | 1000
Total |  | 45000 |  | Total |  |  | 45000
HEAT PUMP OPEX both units |  |  |  | HEAT PUMP OPEX
Cost Component | Notes | Estimated Cost (€) |  | Cost Component |  | % of HP Cost | Estimated Cost (€)
Electricity HP A | COP/Pwr: 3.5/1922 | 1969896.24 |  | Electricity |  | COP: 7.0 | 1106913.6
Electricity HP B | COP/Pwr: 3.0/1026 | 1051567.92 |  | Maintenance |  | Temp lift: 12°C | 80000 |  | Unusually low temperature lift for 65 degree scenario.
Maintenance |  | 80000 |  | Monitoring & Control |  | 1.08 MW added | 20000 |  | Could be reconfigured in several ways.
Monitoring & Control |  | 20000 |  | Insurance & Admin |  | electricity | 15000
Insurance & Admin |  | 15000 |  | Total |  |  | 1221913.6
Total |  | 3136464.16
STORAGE TANK OPEX |  |  |  | STORAGE TANK OPEX
Cost Component |  | Estimated Cost (€) |  | Cost Component |  |  | Estimated Cost (€)
Total OPEX |  | 5000 |  | Total OPEX |  |  | 5000
Total |  | 5000 |  | Total |  |  | 5000
HEAT EXCHANGER OPEX |  |  |  | HEAT EXCHANGER OPEX
Cost Component |  | Estimated Cost (€) |  | Cost Component |  |  | Estimated Cost (€)
Maintenance |  | 10000 |  | Maintenance for both units |  |  | 15000
Total |  | 10000 |  | Total |  |  | 15000
TOTAL SYSTEM OPEX |  |  |  | TOTAL SYSTEM OPEX
Cost Component |  | Estimated Cost (€) |  | Cost Component |  |  | Estimated Cost (€)
Pipe maintenance |  | 45000 |  | Pipe maintenance |  |  | 45000
2 Heat Pumps, electricity and maintenance |  | 3136464.16 |  | Heat Pump electricity and maintenance |  |  | 1221913.6
Storage Tank maintenance |  | 5000 |  | Storage Tank maintenance |  |  | 5000
Heat Exchangers electricity and maintenance |  | 10000 |  | Heat Exchanger electricity and maintenance |  |  | 15000
Total |  | 3186464.16 |  | Total |  |  | 1271913.6
PROJECT CASHFLOW: 30°C scenario
Undiscounted and without inflation
| Current | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10
OPEX |  | 191487.1443 | 191487.1443 | 191487.1443 | 191487.1443 | 191487.1443 | 191487.1443 | 191487.1443 | 191487.1443 | 191487.1443 | 191487.1443
Piping and Trenching |  | -45000 | -45000 | -45000 | -45000 | -45000 | -45000 | -45000 | -45000 | -45000 | -45000
Heat Pumps maintenance |  | -115000 | -115000 | -115000 | -115000 | -115000 | -115000 | -115000 | -115000 | -115000 | -115000
Storage Tank maintenance |  | -5000 | -5000 | -5000 | -5000 | -5000 | -5000 | -5000 | -5000 | -5000 | -5000
Heat Exchanger maintenance |  | -10000 | -10000 | -10000 | -10000 | -10000 | -10000 | -10000 | -10000 | -10000 | -10000
Electricity for Heat Pumps |  | -3021464.16 | -3021464.16 | -3021464.16 | -3021464.16 | -3021464.16 | -3021464.16 | -3021464.16 | -3021464.16 | -3021464.16 | -3021464.16
Cost of carbon displaced (1111 kWh per hour and MW) |  | 2491484.16 | 2491484.16 | 2491484.16 | 2491484.16 | 2491484.16 | 2491484.16 | 2491484.16 | 2491484.16 | 2491484.16 | 2491484.16
Avoided carbon tax (Tons CO2/year) |  | 896467.1443 | 896467.1443 | 896467.1443 | 896467.1443 | 896467.1443 | 896467.1443 | 896467.1443 | 896467.1443 | 896467.1443 | 896467.1443
Natural Gas displaced, MWh per year |  | 77858.88 | 77858.88 | 77858.88 | 77858.88 | 77858.88 | 77858.88 | 77858.88 | 77858.88 | 77858.88 | 77858.88
Natural Gas displaced, Tons CO2 per year |  | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938
CAPEX | -8772000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Piping and Trenching | -272000
Heat Pump(s) | -7920000
Storage Tank | -250000
Heat Exchangers | -330000
Subsidy | -2631600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-off subsidy | -2631600
Carbon subsidy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Savings | -6140400 | 191487.1443 | 191487.1443 | 191487.1443 | 191487.1443 | 191487.1443 | 191487.1443 | 191487.1443 | 191487.1443 | 191487.1443 | 191487.1443
Cumulative Impact | -6140400 | -5948912.8557 | -5757425.7114 | -5565938.567 | -5374451.4227 | -5182964.2784 | -4991477.1341 | -4799989.9898 | -4608502.8454 | -4417015.7011 | -4225528.5568
PAYBACK PERIOD AND OUTLOOK: 30°C scenario
Payback period | 32.0669
System profit after ten years | -4225528.5568
PROJECT CASHFLOW: 65°C scenario
Undiscounted and without inflation
| Current | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10
OPEX |  | 1204570.56 | 1204570.56 | 1204570.56 | 1204570.56 | 1204570.56 | 1204570.56 | 1204570.56 | 1204570.56 | 1204570.56 | 1204570.56
Piping and Trenching |  | -45000 | -45000 | -45000 | -45000 | -45000 | -45000 | -45000 | -45000 | -45000 | -45000
Heat Pumps maintenance |  | -115000 | -115000 | -115000 | -115000 | -115000 | -115000 | -115000 | -115000 | -115000 | -115000
Storage Tank maintenance |  | -5000 | -5000 | -5000 | -5000 | -5000 | -5000 | -5000 | -5000 | -5000 | -5000
Heat Exchanger maintenance |  | -15000 | -15000 | -15000 | -15000 | -15000 | -15000 | -15000 | -15000 | -15000 | -15000
Electricity for Heat Pump |  | -1106913.6 | -1106913.6 | -1106913.6 | -1106913.6 | -1106913.6 | -1106913.6 | -1106913.6 | -1106913.6 | -1106913.6 | -1106913.6
Cost of carbon displaced (1111 kWh per hour and MW) |  | 2491484.16 | 2491484.16 | 2491484.16 | 2491484.16 | 2491484.16 | 2491484.16 | 2491484.16 | 2491484.16 | 2491484.16 | 2491484.16
Avoided carbon tax (Tons CO2/year) |  | 896467.1443 | 896467.1443 | 896467.1443 | 896467.1443 | 896467.1443 | 896467.1443 | 896467.1443 | 896467.1443 | 896467.1443 | 896467.1443
Natural Gas displaced, MWh per year |  | 77858.88 | 77858.88 | 77858.88 | 77858.88 | 77858.88 | 77858.88 | 77858.88 | 77858.88 | 77858.88 | 77858.88
Natural Gas displaced, Tons CO2 per year |  | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938 | 15727.4938
CAPEX | -5242000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Piping and Trenching | -272000
Heat Pump(s) | -4680000
Storage Tank | -250000
Heat Exchangers | -40000
Subsidy | -1572600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-off subsidy | -1572600
Carbon subsidy |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Savings | -3669400 | 1204570.56 | 1204570.56 | 1204570.56 | 1204570.56 | 1204570.56 | 1204570.56 | 1204570.56 | 1204570.56 | 1204570.56 | 1204570.56
Cumulative Impact | -3669400 | -2464829.44 | -1260258.88 | -55688.32 | 1148882.24 | 2353452.8 | 3558023.36 | 4762593.92 | 5967164.48 | 7171735.04 | 8376305.6
PAYBACK PERIOD AND OUTLOOK: 65°C scenario
Payback period | 3.0462
System profit after ten years | 8376305.6
Note on D155: Petter Terenius: Note that the CO2 avoidance is the same as from the 30 degree scenario; it's just that the temp lift is at the DC side.

## System Flow Diagrams
System Flow Diagrams