## Heat Reuse - PUE,WUE,CUE,ERF
Baseline Power Consumptions Calculation for Frankfurt, Germany - Climate Zone: 5A ( Refer ASHRAE 164 & 90.4)
Baseline PUE Calculation without Heat Reuse | [8 empty] | PUE Calculation with Heat Reuse |  |  |  | ERF | Baseline WUE Calculation | [5 empty] | WUE Calculation - Heat Reuse | [5 empty] | Baseline CUE Calculation |  |  |  | CUE Calculation - Heat Reuse
Scenario | Capacity | MLC | ELC | Total Power | PUE | Pump Power | Heat Rejection | Remarks | Heat Repurposed | Pumping Power Requried to RePurpose the heat | Heat ReUse - PUE | Remarks | ReUsed Energy / Total DC energy consumption (IT+Infra) | Total Energy usage | Annual Enery usage | Water Consumed | Annual Water Usage | WUE | Remarks | Total Energy usage | Annual Enery usage | Water Consumed | Annual Water Usage | WUE ↑↓ | Remarks | Annaul Total Power Consumption | kg of CO2 per kWh | Total CO2 Emissions | CUE | Annaul Total Power Consumption | kg of CO2 per kWh | Total CO2 Emissions | CUE ↑↓ | Remarks
| kW | kW | kW | kW | Unitless | kW | kW |  | kW | kW | Unitless |  | Unitless | kW | kWh | liters/kWh | Ltrs | Ltrs/kWh |  | kW | kWh | liters/kWh | Ltrs | Ltrs/kWh |  | kWh |  | (kg) | kg CO₂ / kWh | kWh |  | (kg) | kg CO₂ / kWh
Air Cooled, H1 - Class, Server Inlet 22C for air | 1000 | 420 | 170 | 1590 | 1.59 | 33.6 | 386.4 | MLC - 0.420 & ELC - 0.170 | 386.4 | 6.4681 | 1.0401 | Pump - ∆T = 5°C, H = 25 m, η = 0.70 | 0.24302 | 1590 | 13928400 |  | 5000000 | 0.35898 | humidification, Airflow: 400,000 CFM, 4 L per 1000 CFM per hour, ~4,000 hours/year | 1040.0681 | 9110996.8352 |  | 5000000 | 0 | humidification, Airflow: 400,000 CFM, 4 L per 1000 CFM per hour, ~4,000 hours/year | 13928400 | 0.386 | 5376362.4 | 0.386 | 9110.9968 | 0.386 | 3516.8448 | -0.38575 | 2023 Average: Approximately 354 grams of CO₂ per kWh.
Water Cooled, H1 - Class, Server Inlet 22C for air | 1000 | 310 | 155 | 1465 | 1.465 | 46.5 | 263.5 | MLC - 0.31 & ELC - 0.155 (Reduced because of cooling system) | 263.5 | 4.4109 | 1.0509 | Pump - ∆T = 5°C, H = 25 m, η = 0.70 | 0.17986 | 1465 | 12833400 | 1.8 | 23100120 | 1.8 | Refer the artice for the refrence below | 1050.9109 | 9205979.053 | 1.8 | 16570762.2953 | -0.28265 | Refer the artice for the refrence below | 12833400 | 0.386 | 4953692.4 | 0.386 | 9205.9791 | 0.386 | 3553.5079 | -0.38572
Air Cooled - TC 9.9 W32, 26C for liquid, 75% 25% - Optimized Air + DCLC Hybrid | 1000 | 190 | 155 | 1345 | 1.345 | 34.2 | 155.8 | MLC - 0.19 & ELC - 0.15 (Reduced because of cooling system) - Pumping Share -18% | 155.8 | 2.608 | 1.0368 | Pump - ∆T = 5°C, H = 25 m, η = 0.70 | 0.11584 | 1345 | 11782200 |  | 1500000 | 0.12731 | humidification, Airflow: 120,000 CFM, 4 L per 1000 CFM per hour, ~4,000 hours/year | 1036.808 | 9082438.1649 |  | 1500000 | 0 | humidification, Airflow: 120,000 CFM, 4 L per 1000 CFM per hour, ~4,000 hours/year | 11782200 | 0.386 | 4547929.2 | 0.386 | 9082.4382 | 0.386 | 3505.8211 | -0.3857
Water Cooled - TC 9.9 W32, 26C for liquid, 75% 25% -Water-Cooled + Tower + DCLC | 1000 | 160 | 140 | 1300 | 1.3 | 40 | 120 | MLC - 0.16 & ELC - 0.14 (Reduced because of cooling system) - Pumping Share -25% | 120 | 2.0087 | 1.042 | Pump - ∆T = 5°C, H = 25 m, η = 0.70 | 0.092308 | 1300 | 11388000 | 1.8 | 20498400 | 1.8 | Refer the artice for the refrence below | 1042.0087 | 9127996.5327 | 1.8 | 16430393.7588 | -0.19845 | Refer the artice for the refrence below | 11388000 | 0.386 | 4395768 | 0.386 | 9127.9965 | 0.386 | 3523.4067 | -0.38569
Water Cooled - TC 9.9 W32, 26C for liquid, 75% 25% - Dry Cooler + DCLC | 1000 | 90 | 140 | 1230 | 1.23 | 27 | 63 | MLC - 0.09 & ELC - 0.14 (Reduced because of cooling system) - Pumping Share -25% | 63 | 1.0546 | 1.0281 | Pump - ∆T = 5°C, H = 25 m, η = 0.70 | 0.05122 | 1230 | 10774800 |  | 1500000 | 0.13921 | humidification, Airflow: 120,000 CFM, 4 L per 1000 CFM per hour, ~4,000 hours/year | 1028.0546 | 9005758.1796 |  | 1500000 | 0 | humidification, Airflow: 120,000 CFM, 4 L per 1000 CFM per hour, ~4,000 hours/year | 10774800 | 0.386 | 4159072.8 | 0.386 | 9005.7582 | 0.386 | 3476.2227 | -0.38568
Notes :
1. Additional scenarios modeled: 2. Water-cooled system @ 22°C: PUE = 1.465 3. Air + DCLC Hybrid (75% liquid + 25% Air) @ 26°C: PUE = 1.345 4. Water + DCLC Hybrid: PUE = 1.30 5. Dry Cooler + DCLC (75% Liquid+25%): PUE = 1.23
6. Pump % of MLC:8%
7. Pump Power : for heat reuse P pump = η*1000*m / g⋅H
8. Air-cooled chiller system = 0.02 liters per kWh (only humidity considered
9. Water Cooled chiller system = 1.8 Liters per KWh, refer the below reference
10. CUE Grid Emission Factor (Frankfurt, 2023): 0.386 kg CO₂/kWh (Source: Umweltbundesamt, German EPA)
Links
1. WUE - https://journal.uptimeinstitute.com/dont-ignore-water-consumption/
2. https://dgtlinfra.com/data-center-water-usage/#:~:text=According%20to%20Meta%20Platforms%20(formerly,of%20water%20were%20used%20for