## Assumptions
Parameter | Value | unit | Reference
Electricity Cost | 0.08 | $/kWhe | MSC value supplied
COP Brackish | 3.5 |  | Typical HP used for cooling using air sourced HP, mfg quote
COP Seawater | 3.5 |  | Typical HP with seawter cooling (liquid), mfg quote
COP Produced | 3.3 |  | Typical HP used for cooling using air sourced Heat pump, HT quote
Brackish Feed Salinity | 2000 | mg/l | Typical range 2-10k
Brackish brine Salinity | 150000 | mg/l | Assumes MLD design
Seawater Feed Salinity | 36000 | mg/l | Typically 36-40k
Seawater brine Salinity | 100000 | mg/l | Assumes ocean discharge, 65% recovery
Produced Water Feed | 100000 | mg/l | Typical in Permean basin
Produced Water brine | 200000 | mg/l | Requested recovery 50%
Plant Availability | 98 | % | S/B >95%
Water Sell price brackish | 2.89 | $/m3 | Set by market, used for average baseline, see table below
Water Sell price Seawater | 0.8 | $/m3 | Set by market, used for baseline average, see table below
Water Sell price Produced | 6 | $/m3 | Set by market, used for baseline refernce, see table below
Interest Rate | 6 | % | Project Finance rate assumption
Plant Life | 20 | years | Typical for brackish and seawater, 10yrs for oil and gas
Heat Pump Capex | 250 | $/kWhth | From table in Text, IEA Conf. Proc.
FO Electrical (Brackish & Seawater) | 1.3 | kWh/m3 | From PFD Tab
FO Electrical (Produced) | 4.5 | kWh/m3 | From PFD Tab
FO Thermal (Brackish & Seawater) | 35 | kWh/m3 | From PFD tab
FO Thermal (Produced) | 50 | kWh/m3 | From PFD Tab
RO Electrical (MLD brackish) | 12.5 | kWh/m3 | From GWI reference in Workbook
UPRO Electrical (Sea) | 5.7 | kWh/m3 | From GWI reference in Workbook
UPRO&MVR Electrical (O&G) | 28.7 | kWh/m3 | From GWI reference in Workbook
City | Water Source | Estimated Lowest Tier Cost (USD/m³)
Phoenix, AZ | Surface & Groundwater | 1.96
El Paso, TX | Brackish Groundwater (Desal.) | 5.43
Midland, TX | Groundwater | 2.99
Albuquerque, NM | Surface & Groundwater | 1.49
Reno, NV | Surface Water | 1.79 |  | The average multiplier that cities charge consumers over the estimated Levelized Cost of Water (LCOW) from brackish desalination (assumed at $0.50/m³) is approximately 5.78×.
Sonoma, CA | Surface Water | 1.7
Fresno, CA (est.) | Surface & Groundwater | 2.5 |  | You can explore the detailed comparison in the table provided, which includes each city’s markup over the base LCOW. Let me know if you'd like the same analysis using seawater desalination LCOW or for higher usage tiers.
San Francisco, CA | Surface Water | 8.2
Monterey, CA | Surface & Groundwater | 5.29
San Angelo, TX | Brackish Groundwater (Desal.) | 1.98
Alamogordo, NM | Brackish Groundwater (Desal.) | 1.98
Odessa, TX | Brackish Groundwater (Desal.) | 1.98
San Antonio, TX | Brackish Groundwater (Desal.) | 2
Los Angeles, CA | Brackish & Surface Water | 3
Oxnard, CA | Brackish Groundwater (Desal.) | 2.5
Tampa, FL | Brackish & Surface Water | 2.2
Jacksonville, FL | Brackish & Surface Water | 2.1
| Average | 2.8876
City | Seawater | Est lowest Tier (USD/m3)
San Diego | Seawater
Miami | Seawater
Corpus Christi | Seawater
Virginia Beach | Seawater
Honolulu | Seawater
City | Produced Water | Est lowest Tier (USD/m3)

## Produced
Variable | Value | Unit | Reference
DC Cooling Req | 1 | MW | Design Point
DC Waste Heat Avail | 1.4599 | MW | From Quote by HP mfg.
FO & RO Plant Size | 700.7299 | m3/day | Based on heat avail.
FO Plant CAPEX | 2557664.2336 |  | Derived by Trevi
FO Electrical Energy | 4.5 | kWh/m3 | Assumption tab
FO Thermal Energy | 50 | kWh/m3 | Assumption tab
COP heat Pump with FO | 3.3 |  | Calculated from lift and industry quote
FO
Annual Electricity cost | 92075.9124 |  | Assumption tab & Calculated
Annual FO Thermal Energy Costs (No WH & DC) | 328837.3047 |  | Calculated from Dallas Table below
Annual FO Thermal Energy Costs( 30C WH) | 308321.1679 |  | Calculated from Dallas Table below
Annual FO Thermal Energy Costs (45C WH) | 231240.8759 |  | Calculated from Dallas Table below
FO CAPEX | 2557664.2336 |  | Calculated
Annual FO CAPEX Cost | 219886.8113 |  | Calculated
HEAT Pump CAPEX | 500000 |  | Calculated
Annual HP CAPEX | 42985.8635 |  | From Ref in Document
Annual FO Plant OPEX Cost | 256477.454 |  | Calculated
UPRO+MVR
Annual Electricity cost | 587239.708 |  | Assumptions tab
RO CAPEX Cost | 2732846.7153 |  | GWI databook
Annual CAPEX Cost | 234947.5518 |  | Calculated
Annual OPEX Cost | 327941.6058 |  | GWI databook
Recovery rate | 50% |  | Calculated
For Dallas
LCOW FO (no DC) | 3.6763 |  | =Annualized (Electricity Cost + Thermal costs (no HP)+ FO CAPEX+FO OPEX+ HeatPump CAPEX)/1000
LCOW FO (+ DCWH @30 deg C) | 3.596 |  | =Annualized (Electricity Cost + Thermal costs (w HP @30 deg C)+ FO CAPEX+ OPEX+ HeatPump CAPEx)/1000
LCOW FO (+ DCWH @45 degC + 33 DegC Ret) | 3.2947 |  | =Annualized (Electricity Cost + Thermal costs (w HP@ 45 deg C)+ FO CAPEX+ OPEX+ HeatPump CAPEX)/1000
LCOW UHPRO | 4.4968 |  | =Annualized (RO Electricity Cost + RO CAPEX+ RO OPEX)/1000
Dallas | With 30C DC Heat | $/m3 | $/bbl | With 45C DC Heat | $/m3 | $/bbl | Heat Pump Savings with DC Waste heat vs Produced water sourced HP ( 30C DC )
| LCOW FO (no DC) | 3.6763 | 0.59294 | LCOW FO (no DC) | 3.596 | 0.58001
| LCOW FO (+ DC) | 3.596 | 0.58001 | LCOW FO (+ DC) | 3.2947 | 0.5314 | Location | jan | feb | march | April | may | june | july | Aug | Sep | Oct | Nov | Dec | Annual Energy Used (MWH)
| LCOW UPRO+MVR | 4.4968 | 0.72529 | LCOW UPRO+MVR | 4.4968 | 0.72529 | Dallas | 8.6 | 10.3 | 14.6 | 18.7 | 23.3 | 27.8 | 30.3 | 30.3 | 26.9 | 20.9 | 14.7 | 9
[7 empty] | Ambient HP COP | 2.6757 | 2.7327 | 2.8886 | 3.0547 | 3.2654 | 3.5016 | 3.6482 | 3.6482 | 3.4517 | 3.152 | 2.8924 | 2.6889 | Ref; ASHRAE, IAE, US DOE sources
Annual Thermal FO No DC | 328837.3047 | [5 empty] | COP of DC waste Heat (53% of Carnot cycle (air) | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | Mfg data
Annual Thermal 30 Deg | 308321.1679 |  | Table right 30C |  |  |  | FO Energy No DC WH | 405.9279 | 358.9874 | 376.0069 | 344.0912 | 332.6215 | 300.1749 | 288.11 | 288.11 | 304.5183 | 344.5899 | 363.3951 | 403.9332 | 4110.4663
Annual Thermal 45 | 231240.8759 |  | Table right 45C |  |  |  | FO Energy w DC 30 deg C | 329.1307 | 297.2794 | 329.1307 | 318.5136 | 329.1307 | 318.5136 | 318.5136 | 318.5136 | 318.5136 | 329.1307 | 318.5136 | 329.1307 | 3854.0146
Heat Pump Savings with DC Waste heat vs Produced sourced HP (45C DC )
#VALUE!
[7 empty] | Location | jan | feb | march | April | may | june | july | Aug | Sep | Oct | Nov | Dec | Annual Energy Used (MWH)
[7 empty] | Dallas | 8.6 | 10.3 | 14.6 | 18.7 | 23.3 | 27.8 | 30.3 | 30.3 | 26.9 | 20.9 | 14.7 | 9
[7 empty] | Ambient HP COP | 2.6757 | 2.7327 | 2.8886 | 3.0547 | 3.2654 | 3.5016 | 3.6482 | 3.6482 | 3.4517 | 3.152 | 2.8924 | 2.6889 | Ref; ASHRAE, IAE, US DOE sources
[7 empty] | COP of DC waste Heat (53% of Carnot cycle (air) | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | Mfg data
[7 empty] | FO Energy No DC WH | 405.9279 | 358.9874 | 376.0069 | 344.0912 | 332.6215 | 300.1749 | 288.11 | 288.11 | 304.5183 | 344.5899 | 363.3951 | 403.9332 | 4110.4663
[7 empty] | FO Energy w DC 45 deg C | 246.848 | 222.9595 | 246.848 | 238.8852 | 246.848 | 238.8852 | 238.8852 | 238.8852 | 238.8852 | 246.848 | 238.8852 | 246.848 | 2890.5109

## CAPEX & Opex produced
Location Data - Monthly Average Ambient Temperature and COP calculations
Location | Jan | Feb | Mar | April | May | Jun | Jul | Aug | Sept | Oct | Nov | Dec
Dallas | 8.6 | 10.3 | 14.6 | 18.7 | 23.3 | 27.8 | 30.3 | 30.3 | 26.9 | 20.9 | 14.7 | 9
HP COP* | 2.6757 | 2.7327 | 2.8886 | 3.0547 | 3.2654 | 3.5016 | 3.6482 | 3.6482 | 3.4517 | 3.152 | 2.8924 | 2.6889
Houston | 11.7 | 13.1 | 17.2 | 21.3 | 25.5 | 28.8 | 30.5 | 30.7 | 28 | 23.1 | 17.3 | 12.6
HP COP* | 2.7816 | 2.8322 | 2.9918 | 3.1703 | 3.3767 | 3.5588 | 3.6605 | 3.6728 | 3.5129 | 3.2556 | 2.9959 | 2.814
Denver | -1 | 1.1 | 5.3 | 9.9 | 14.1 | 20.1 | 23.4 | 22.6 | 17.8 | 11.8 | 4.4 | -0.8
HP COP* | 2.3934 | 2.4499 | 2.5714 | 2.7191 | 2.8696 | 3.1159 | 3.2703 | 3.2315 | 3.0166 | 2.7852 | 2.5444 | 2.3987
calculations:
* COP calculated is ratio of COP (actual)/COP (datacenter)* COP of manufacturer: COP = Thot/(Thot-Tcold) (actual) / COP (datacenter) * COP manufacturer
* ASHRAE D-CCC23-21.pdf
Data Center Ideal Carnot COP @ 30C:
5.5 |  |  |  | 90C = Avg Hot of FO and 24C = Avg Cold @30C DC |  |  |  | (30C+18C)/2=24C |  | COP @30C | 3.3
Data Center Ideal Carnot COP @ 45C: | [9 empty] | COP @45C | 4.4
7.1176 |  |  |  | 90C = Avg Hot of FO and 31.5C = Avg Cold @45C DC |  |  |  | (45C+33C)/2 = 39C
Data Center Ambient COP
(273+90)/((273+90)-(273+T)) |  |  |  | Use to calculate ambient produced water COP
363/(363-(273+T))
Actual COP is then:: COP(mfg)* COPambient (ideal carnot)/COP DC i(deal carnot)
Location | Jan | Feb | Mar | April | May | Jun | Jul | Aug | Sept | Oct | Nov | Dec
Abu Dhabi | 21.5 | 22.3 | 25.3 | 29.6 | 33.7 | 35.8 | 37.4 | 37.3 | 35.5 | 31.9 | 27.4 | 23.4
HP COP* | 3.1796 | 3.2171 | 3.3663 | 3.606 | 3.8686 | 4.0185 | 4.1407 | 4.1328 | 3.9963 | 3.7487 | 3.4792 | 3.2703
Riyadh | 14 | 16.4 | 20.2 | 25.2 | 30.2 | 33.6 | 35.6 | 35.3 | 32.4 | 27.3 | 21.4 | 16
HP COP* | 2.8658 | 2.9592 | 3.1203 | 3.3611 | 3.6421 | 3.8617 | 4.0037 | 3.9817 | 3.7812 | 3.4737 | 3.1749 | 2.9432
muscat | 22.4 | 23.7 | 26.9 | 31.4 | 35.6 | 36.8 | 36.4 | 35.1 | 34.1 | 31.6 | 26.9 | 23.4
HP COP* | 3.2219 | 3.2851 | 3.4517 | 3.7167 | 4.0037 | 4.094 | 4.0634 | 3.9672 | 3.8962 | 3.7295 | 3.4517 | 3.2703
calculations:
* COP calculated is ratio of COP (actual)/COP (datacenter)* COP of manufacturer: COP = Thot/(Thot-Tcold) (actual) / COP (datacenter) * COP manufacturer
* ASHRAE D-CCC23-21.pdf
Data Center Ideal Carnot COP @ 30C:
5.5 |  |  |  | 90C = Avg Hot of FO and 24C = Avg Cold @30C DC |  |  |  | (30C+18C)/2=24C |  | COP @30C | 3.3
Data Center Ideal Carnot COP @ 45C: | [9 empty] | COP @45C | 4.4
7.1176 |  |  |  | 90C = Avg Hot of FO and 31.5C = Avg Cold @45C DC |  |  |  | (45C+33C)/2 = 39C
Hot side = 95 & return = 85 = 90 deg C average
Data Center Ambient COP
(273+90)/((273+90)-(273+T)) |  |  |  | Use to calculate ambient produced water COP
363/(363-(273+T))