## PFD Brackish_Rev1
Microsoft 1,000 m3/Day Brackish System
Supernatant
Product
Water
Dilute
Feedwater | [17 empty] | Solution
Strong Solution
Brine
Brine
[28 empty] | 33,45C |  | 18,33C
DataCenter Heat Source
System Conditions | Design Conditions
Stream Description | Feedwater | Filtered Feed | Feed Water to FO Membranes | Diluted Draw Solution | Diluted Draw to HXs | Diluted Draw to Water / Weak HX-2 | Diluted Draw and Nano Reject to HX-2 | Diluted Draw to Strong / Weak HX-1 | Warm Dilute Draw from HX-2 | Warm Dilute Draw from HX-1 | Warm Dilute Draw to Boost HX-3 | Hot Dilute Draw | Hot Water Return from Boost HX-3 | Hot Water Feed to Boost HX-3 | Hot Conc. Draw | Cooled Conc Draw | Super-natant | Cooled Super-natant | Cooling Water to HX-4 | Return Cooling Water from HX-4 | Chilled Super-natant | Pressurized Super-natant to Nanofilter | Nanofilter Permeate | Nanofilter Reject | Pressurized RO Feed | Low Pressure RO Permeate | Low Pressure RO Reject | Remineralized Product Water | FO Membrane Brine | System Brine | Chilled Strong Draw | Return Cooling Water from HX-5 | Cooling Water to HX-5 |  | Chemical Injections | Sulfuric Acid (35%) | Sodium Hypo Chlorite to Feed Water (5%) | Sodium Meta Bisulfite (10%) | Sodium Hydroxide to Weak Draw (5%) | Sodium Hydroxide to Product Water (5%) | Calcium Chloride | Sodium Hypo Chlorite to Product Water (12%) | Scale Inhibitor
Parameter | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 |  |  | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41
Temperature (deg C) | 6 - 33 | 6 - 33 | 6 - 33 | 33.3081 | 33.3081 | 33.3081 | 33.4007 | 33.3081 | 75.4 | 72.6 | 73.3047 | 85 | 80 | 90 | 85 | 38.34 | 85 | 42.51 | 25 | 35 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 99.5487 | 99.5487 | 30 | 32 | 25 |  |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Flowrate (m3/h) | 43.8596 | 43.8596 | 43.8596 | 220.6966 | 220.6966 | 53.9049 | 56.0979 | 166.7917 | 56.0979 | 166.7917 | 222.8895 | 222.8895 | 177.2083 | 177.2083 | 179.0299 | 179.0299 | 43.8596 | 43.8596 | 54.5833 | 54.5833 | 43.8596 | 43.8596 | 41.6667 | 2.193 | 41.6667 | 41.6667 | 0 | 41.6667 | 2.193 | 2.193 | 179.0299 | 131.25 | 131.25 |  | ml/min | 166.93 | 69.21 | 785.15 | 308.78 | 54.17 | 48.37 | 10.38 | 9.64
Mass Flowrate (kg/hr) | 43945.1754 | 43945.1754 | 43945.1754 | 237557.3945 | 237557.3945 | 58023.1344 | 60323.0149 | 179534.2601 | 60323.0149 | 179534.2601 | 239857.275 | 239857.275 | 171537.6667 | 171537.6667 | 194386.1103 | 194386.1103 | 43015.2193 | 43015.2193 | 54348.625 | 54348.625 | 43015.2193 | 43015.2193 | 41402.0083 | 1613.211 | 41402.0083 | 41487.5 | -85.4917 | 41487.5 | 2288.6609 | 2264.2497 | 194386.1103 | 131221.4531 | 131221.4531 |  | g/min | 198.41 | 69.44 | 810.19 | 316.67 | 55.56 | 103.99 | 10.42 | 11.55
Pressure (psi) | 30 | 27 | 27 | 5 | 23 | 23 | 23 | 23 | 19 | 19 | 19 | 15 | 3 | 5 | 15 | 10 | 15 | 13 | 5 | 3 | 11 | 110 | 5 | 23 | 105 | 10 | 10 | 5 | 10 | 10 | 6 | 3 | 5 |  |  | 27 | 27 | 27 | 5 | 5 | 5 | 5 | 27
Pressure (bar) | 2.0684 | 1.8616 | 1.8616 | 0.34474 | 1.5858 | 1.5858 | 1.5858 | 1.5858 | 1.31 | 1.31 | 1.31 | 1.0342 | 0.20684 | 0.34474 | 1.0342 | 0.68948 | 1.0342 | 0.89632 | 0.34474 | 0.20684 | 0.75842 | 7.5842 | 0.34474 | 1.5858 | 7.2395 | 0.68948 | 0.68948 | 0.34474 | 0.68948 | 0.68948 | 0.41369 | 0.20684 | 0.34474 |  |  | 1.8616 | 1.8616 | 1.8616 | 0.34474 | 0.34474 | 0.34474 | 0.34474 | 1.8616
TDS (mg/l) | 5000 | 5000 | 5000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 100000 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Polymer Concentration (wt%) | 0% | 0% | 0% | 60.43% | 60.43% | 60.43% | 58.85% | 60.43% | 58.85% | 60.43% | 60.04% | 60.04% | 0% | 0% | 74.5% | 74.5% | 1% | 1% | 0% | 0% | 1% | 1% | 0% | 20% | 0% | 0% | 0% | 0% | 0% | 0% | 74.5% | 0% | 0%
pH | 7.8 | 7.8 | 6.5 | 6.5 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Heat Transfer (kW) | [8 empty] | 2123.9346 | 5939.7885 |  | 2002.3667 |  | -2002.7023 |  | -5940.5843 |  | -2125.8645 |  | 630.897 | -632.7718 | [9 empty] | -1061.819 |  | 1060.861
41.6667 | m3/h | 41024.2489 | [16 empty] | 0 | [5 empty] | 0
Density | [8 empty] | 1026 | 1026 | 1026 | 1024 | 1025 | 1025 | 1078.05 | 1076.13 | 1076.13 | 1076.13 | 1076.13 | 1076.13 | 1076.13 | 1076.13 | 1083.27 | 1083.27 | 972 | 990.2 | 993.4 | 993.4 | 993.4 | 1020 | 1025.1 | 968 | 968.8
m3/day per m3 | [8 empty] | 2.32 | 1.18 | 1.14 | 1.18 | 1.14 | 2.32 | 3.73 | 3.9 | 1.84 | 2.06 | 1.84 | 2.06 | 3.9 | 3.9 | 2.73 | 2.73 | 1.18 | 1.18 | 1.18 | 1 | 0.18 | 1.32 | 1.32 | 17.9 | 17.9
l/min | [8 empty] | 80.5556 | 40.9722 | 39.5833 | 40.9722 | 39.5833 | 80.5556 | 129.5139 | 135.4167 | 63.8889 | 71.5278 | 63.8889 | 71.5278 | 135.4167 | 135.4167 | 94.7917 | 94.7917 | 40.9722 | 40.9722 | 40.9722 | 34.7222 | 6.25 | 45.8333 | 45.8333 | 621.5277 | 621.5277
0.69444
Trevi Systems, Inc. Proprietary and Confidential | [11 empty] | 238244.064 |  |  |  | Trevi Systems |  | #VALUE!
Membrane
Draw Soln
Fresh Water
Water
Strong
Solution
Separator
Heated
Water/ Weak HX-3
Water/ Weak HX-2
Carbon / Remin.
Heat Pump
1
26
30
22
8
16
9
10
14
15
12
13
11
29
28
2
25
17
Nanofilter
6
Low Pressure RO
Filtration
3
4
5
7
27
34
35
36
37
38
39
40
41
Strong/ Weak HX-1
Supt/ Cold Water HX-4
20
18
Cooler
19
21
23
24
Cooler
Strong/ Cold Water HX-5
31
33
32

## PFD Brackish
Microsoft 1,000 m3/Day System
Supernatant
Product
Water
Dilute
Feedwater | [17 empty] | Solution
Strong Solution
Brine
Brine
System Conditions | Design Conditions
Stream Description | Feedwater | Filtered Feed | Feed Water to FO Membranes | Diluted Draw Solution | Diluted Draw to HXs | Diluted Draw to Water / Weak HX-2 | Diluted Draw and Nano Reject to HX-2 | Diluted Draw to Strong / Weak HX-1 | Warm Dilute Draw from HX-2 | Warm Dilute Draw from HX-1 | Warm Dilute Draw to Boost HX-3 | Hot Dilute Draw | Hot Water Return from Boost HX-3 | Hot Water Feed to Boost HX-3 | Hot Conc. Draw | Cooled Conc Draw | Super-natant | Cooled Super-natant | Cooling Water to HX-4 | Return Cooling Water from HX-4 | Chilled Super-natant | Pressurized Super-natant to Nanofilter | Nanofilter Permeate | Nanofilter Reject | Pressurized RO Feed | Low Pressure RO Permeate | Low Pressure RO Reject | Remineralized Product Water | FO Membrane Brine | System Brine | Chilled Strong Draw | Return Cooling Water from HX-5 | Cooling Water to HX-5 |  | Chemical Injections | Sulfuric Acid (35%) | Sodium Hypo Chlorite to Feed Water (5%) | Sodium Meta Bisulfite (10%) | Sodium Hydroxide to Weak Draw (5%) | Sodium Hydroxide to Product Water (5%) | Calcium Chloride | Sodium Hypo Chlorite to Product Water (12%) | Scale Inhibitor
Parameter | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 |  |  | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41
Temperature (deg C) | 6 - 33 | 6 - 33 | 6 - 33 | 33.3081 | 33.3081 | 33.3081 | 33.4007 | 33.3081 | 75.4 | 72.6 | 73.3047 | 85 | 80 | 90 | 85 | 38.34 | 85 | 42.51 | 25 | 35 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 99.5487 | 99.5487 | 30 | 32 | 25 |  |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Flowrate (m3/h) | 43.8596 | 43.8596 | 43.8596 | 220.6966 | 220.6966 | 53.9049 | 56.0979 | 166.7917 | 56.0979 | 166.7917 | 222.8895 | 222.8895 | 177.2083 | 177.2083 | 179.0299 | 179.0299 | 43.8596 | 43.8596 | 54.5833 | 54.5833 | 43.8596 | 43.8596 | 41.6667 | 2.193 | 41.6667 | 41.6667 | 0 | 41.6667 | 2.193 | 2.193 | 179.0299 | 131.25 | 131.25 |  | ml/min | 166.93 | 69.21 | 785.15 | 308.78 | 54.17 | 48.37 | 10.38 | 9.64
Mass Flowrate (kg/hr) | 43945.1754 | 43945.1754 | 43945.1754 | 237557.3945 | 237557.3945 | 58023.1344 | 60323.0149 | 179534.2601 | 60323.0149 | 179534.2601 | 239857.275 | 239857.275 | 171537.6667 | 171537.6667 | 194386.1103 | 194386.1103 | 43015.2193 | 43015.2193 | 54348.625 | 54348.625 | 43015.2193 | 43015.2193 | 41402.0083 | 1613.211 | 41402.0083 | 41487.5 | -85.4917 | 41487.5 | 2288.6609 | 2264.2497 | 194386.1103 | 131221.4531 | 131221.4531 |  | g/min | 198.41 | 69.44 | 810.19 | 316.67 | 55.56 | 103.99 | 10.42 | 11.55
Pressure (psi) | 30 | 27 | 27 | 5 | 23 | 23 | 23 | 23 | 19 | 19 | 19 | 15 | 3 | 5 | 15 | 10 | 15 | 13 | 5 | 3 | 11 | 110 | 5 | 23 | 105 | 10 | 10 | 5 | 10 | 10 | 6 | 3 | 5 |  |  | 27 | 27 | 27 | 5 | 5 | 5 | 5 | 27
Pressure (bar) | 2.0684 | 1.8616 | 1.8616 | 0.34474 | 1.5858 | 1.5858 | 1.5858 | 1.5858 | 1.31 | 1.31 | 1.31 | 1.0342 | 0.20684 | 0.34474 | 1.0342 | 0.68948 | 1.0342 | 0.89632 | 0.34474 | 0.20684 | 0.75842 | 7.5842 | 0.34474 | 1.5858 | 7.2395 | 0.68948 | 0.68948 | 0.34474 | 0.68948 | 0.68948 | 0.41369 | 0.20684 | 0.34474 |  |  | 1.8616 | 1.8616 | 1.8616 | 0.34474 | 0.34474 | 0.34474 | 0.34474 | 1.8616
TDS (mg/l) | 5000 | 5000 | 5000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 100000 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Polymer Concentration (wt%) | 0% | 0% | 0% | 60.43% | 60.43% | 60.43% | 58.85% | 60.43% | 58.85% | 60.43% | 60.04% | 60.04% | 0% | 0% | 74.5% | 74.5% | 1% | 1% | 0% | 0% | 1% | 1% | 0% | 20% | 0% | 0% | 0% | 0% | 0% | 0% | 74.5% | 0% | 0%
pH | 7.8 | 7.8 | 6.5 | 6.5 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Heat Transfer (kW) | [8 empty] | 2123.9346 | 5939.7885 |  | 2002.3667 |  | -2002.7023 |  | -5940.5843 |  | -2125.8645 |  | 630.897 | -632.7718 | [9 empty] | -1061.819 |  | 1060.861
41.6667 | m3/h | 41024.2489 | [16 empty] | 0 | [5 empty] | 0
Density | [8 empty] | 1026 | 1026 | 1026 | 1024 | 1025 | 1025 | 1078.05 | 1076.13 | 1076.13 | 1076.13 | 1076.13 | 1076.13 | 1076.13 | 1076.13 | 1083.27 | 1083.27 | 972 | 990.2 | 993.4 | 993.4 | 993.4 | 1020 | 1025.1 | 968 | 968.8
m3/day per m3 | [8 empty] | 2.32 | 1.18 | 1.14 | 1.18 | 1.14 | 2.32 | 3.73 | 3.9 | 1.84 | 2.06 | 1.84 | 2.06 | 3.9 | 3.9 | 2.73 | 2.73 | 1.18 | 1.18 | 1.18 | 1 | 0.18 | 1.32 | 1.32 | 17.9 | 17.9
l/min | [8 empty] | 80.5556 | 40.9722 | 39.5833 | 40.9722 | 39.5833 | 80.5556 | 129.5139 | 135.4167 | 63.8889 | 71.5278 | 63.8889 | 71.5278 | 135.4167 | 135.4167 | 94.7917 | 94.7917 | 40.9722 | 40.9722 | 40.9722 | 34.7222 | 6.25 | 45.8333 | 45.8333 | 621.5277 | 621.5277
0.69444
Trevi Systems, Inc. Proprietary and Confidential | [11 empty] | 238244.064 |  |  |  | Trevi Systems |  | #VALUE!
Membrane
Draw Soln
Fresh Water
Water
Strong
Solution
Separator
Heated
Water/ Weak HX-3
Water/ Weak HX-2
Carbon / Remin.
Heat Pump
1
26
30
22
8
16
9
10
14
15
12
13
11
29
28
2
25
17
Nanofilter
6
Low Pressure RO
Filtration
3
4
5
7
27
34
35
36
37
38
39
40
41
Strong/ Weak HX-1
Supt/ Cold Water HX-4
20
18
Cooler
19
21
23
24
Cooler
Strong/ Cold Water HX-5
31
33
32