## Assumptions
Parameter | Value | unit | Reference
Electricity Cost | 0.08 | $/kWhe | MSC value supplied
COP Brackish | 3.5 |  | Typical HP used for cooling using air sourced HP, mfg quote
COP Seawater | 3.5 |  | Typical HP with seawter cooling (liquid), mfg quote
COP Produced | 3.2 |  | Typical HP used for cooling using air sourced Heat pump, HT quote
Brackish Feed Salinity | 2000 | mg/l | Typical range 2-10k
Brackish brine Salinity | 150000 | mg/l | Assumes MLD design
Seawater Feed Salinity | 35000 | mg/l | Typically 36-40k
Seawater brine Salinity | 100000 | mg/l | Assumes ocean discharge, 65% recovery
Produced Water Feed | 100000 | mg/l | Typical in Permean basin
Produced Water brine | 200000 | mg/l | Requested recovery 50%
Plant Availability | 98 | % | S/B >95%
Interest Rate | 6 | % | Project Finance rate assumption
Plant Life | 20 | years | Typical for brackish and seawater, 10yrs for oil and gas
Heat Pump Capex | 250 | $/kWhth | From table in Text, IEA Conf. Proc.
FO Electricicty (MLD) | 1.3 | kWh/m3 | From PFD Tab
FO Thermal brackish& Sea | 35 | kWh/m3 | From PFD tab
FO Thermal, Produced | 50 | kWh/m3 | From PFD Tab
RO Electrical (MLD brackish) | 12.5 | kWh/m3 | From GWI refernce in Workbook
UPRO Electrical (Sea) | 5.7 | kWh/m3 | From GWI refernce in Workbook
RO Electrical (O&G) | 23 | kWh/m3 | From GWI refernce in Workbook

## Seawater Report_SanDiego
Variable | Value | Unit | Reference
DC Cooling Req | 1 | MW | Design Point
DC Waste Heat Avail | 1.4599 | MW | From Quote by HP mfg.
FO & RO Plant Size | 1000 | m3/day | Based on heat avail.
FO Plant CAPEX | 1651720.5422 |  | Derived by Trevi
FO Electrical Energy | 1.3 | kWh/m3 | Assumption tab
FO Thermal Energy | 35 | kWh/m3 | Assumption tab
COP heat Pump with FO | 3.5 |  | Calculated from lift and industry quote
FO
Annual Electricity cost | 37960 |  | Assumption tab & Calculated
Annual FO Thermal Energy Costs (No WH & DC) | 330132.9794 |  | Calculated from San Diego Table below
Annual FO Thermal Energy Costs( 30C WH) | 290702.8154 |  | Calculated from San Diego Table below
Annual FO Thermal Energy Costs (45C WH) | 211420.2294 |  | Calculated from San Diego Table below
FO CAPEX | 1651720.5422 |  | Calculated
Annual FO CAPEX Cost | 42985.8635 |  | Calculated
HEAT Pump CAPEX | 500000 |  | Calculated
Annual HP CAPEX | 42985.8635 |  | From Ref in Document
Annual FO Plant OPEX Cost | 143699.6872 |  | Calculated
UHPRO
Annual Electricity cost | 166440 |  | Assumptions tab
RO CAPEX Cost | 1500000 |  | GWI databook
Annual CAPEX Cost | 128957.5905 |  | Calculated
Annual OPEX Cost | 130500 |  | GWI databook
Recovery rate | 65% |  | Calculated
LCOW FO (no DC) | 1.6377 | /m3 | =Annualized (Electricity Cost + Thermal costs (no HP)+ FO CAPEX+FO OPEX+ HeatPump CAPEX)/1000
LCOW FO (+ DCWH @30 deg C) | 1.5297 | /m3 | =Annualized (Electricity Cost + Thermal costs (w HP @30 deg C)+ FO CAPEX+ OPEX+ HeatPump CAPEx)/1000
LCOW FO (+ DCWH @45 degC + 33 DegC Ret) | 1.3125 | /m3 | =Annualized (Electricity Cost + Thermal costs (w HP@ 45 deg C)+ FO CAPEX+ OPEX+ HeatPump CAPEX)/1000
LCOW UHPRO | 1.1668 | /m3 | =Annualized (RO Electricity Cost + RO CAPEX+ RO OPEX)/1000
Heat Pump Savings with DC Waste heat vs sea water sourced HP ( 30C DC )
Levelized Cost of Water - LCOW ($/m3) | LCOW FO (No WH) | LCOW (with DC WH) | LCOW (with DC WH) | LCOW RO | Location | jan | feb | march | April | may | june | july | Aug | Sep | Oct | Nov | Dec | Annual Energy Used (MWH)
Location / Temperature | Ambient | 30C In + 18C Out | 45C In + 33C Out | Ambient | San Diego, CA | 14 | 14 | 14 | 15.5 | 16.5 | 18 | 19 | 20 | 19 | 17.5 | 16 | 15
San Diego, CA | 1.6377 | 1.5297 | 1.3125 | 1.1668 | Seawater COP | 2.9615 | 2.9615 | 2.9615 | 3.0315 | 3.08 | 3.1557 | 3.2083 | 3.2627 | 3.2083 | 3.1301 | 3.0556 | 3.0078 | Ref; ASHRAE, IAE, US DOE sources - see Capex and opex calcs.
[5 empty] | COP of DC waste Heat (53% of Carnot cycle (water) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | Mfg data
[5 empty] | FO Energy No DC WH | 366.7457 | 331.2541 | 366.7457 | 346.7248 | 352.6401 | 333.0742 | 327.614 | 322.1538 | 327.614 | 346.9978 | 343.9947 | 361.1034 | 4126.6622
[5 empty] | FO Energy w DC 30 deg C | 310.3233 | 280.292 | 310.3233 | 300.3128 | 310.3233 | 300.3128 | 300.3128 | 300.3128 | 300.3128 | 310.3233 | 300.3128 | 310.3233 | 3633.7852
Heat Pump Savings with DC Waste heat vs seawater sourced HP (45C DC )
#VALUE!
[6 empty] | Location | jan | feb | march | April | may | june | july | Aug | Sep | Oct | Nov | Dec | Annual Energy Used (MWH)
[5 empty] | San Diego, CA | 14 | 14 | 14 | 15.5 | 16.5 | 18 | 19 | 20 | 19 | 17.5 | 16 | 15
[5 empty] | Sea Water HP COP | 2.9615 | 2.9615 | 2.9615 | 3.0315 | 3.08 | 3.1557 | 3.2083 | 3.2627 | 3.2083 | 3.1301 | 3.0556 | 3.0078 | Ref; ASHRAE, IAE, US DOE sources - see Capex and opex calcs.
[5 empty] | DC Waste Heat COP | 4.8125 | 4.8125 | 4.8125 | 4.8125 | 4.8125 | 4.8125 | 4.8125 | 4.8125 | 4.8125 | 4.8125 | 4.8125 | 4.8125 | Mfg data
[5 empty] | FO Energy No DC WH | 366.7457 | 331.2541 | 366.7457 | 346.7248 | 352.6401 | 333.0742 | 327.614 | 322.1538 | 327.614 | 346.9978 | 343.9947 | 361.1034 | 4126.6622
[5 empty] | FO Energy w DC 30 deg C | 225.6896 | 203.8487 | 225.6896 | 218.4093 | 225.6896 | 218.4093 | 218.4093 | 218.4093 | 218.4093 | 225.6896 | 218.4093 | 225.6896 | 2642.7529

## COP & Temps SWFO
Location Data - Monthly Average Seawater Temperature and COP calculations
| Location | Jan | Feb | Mar | April | May | Jun | Jul | Aug | Sept | Oct | Nov | Dec
| San Diego, CA | 14 | 14 | 14 | 15.5 | 16.5 | 18 | 19 | 20 | 19 | 17.5 | 16 | 15 | Average Seawater temperature
| HP COP* | 2.9615 | 2.9615 | 2.9615 | 3.0315 | 3.08 | 3.1557 | 3.2083 | 3.2627 | 3.2083 | 3.1301 | 3.0556 | 3.0078 | calculated COP for 30C heat
| Miami, Fl | 24 | 24 | 24.6 | 25.6 | 26.9 | 28.5 | 29.5 | 29.9 | 29.4 | 28.2 | 26.5 | 25.3
| HP COP* | 3.5 | 3.5 | 3.5386 | 3.6049 | 3.6948 | 3.8119 | 3.8889 | 3.9206 | 3.881 | 3.7894 | 3.6667 | 3.5847
| Corpus Christi, TX | 17.2 | 16.7 | 18.9 | 22.8 | 26.1 | 28.9 | 30 | 30 | 29.4 | 26.1 | 22.2 | 19.4
| HP COP* | 3.1149 | 3.0899 | 3.203 | 3.4253 | 3.6389 | 3.8423 | 3.9286 | 3.9286 | 3.881 | 3.6389 | 3.3891 | 3.2299
| Virginia Beach, VA | 7.5 | 5.2 | 7 | 11.8 | 17.3 | 22.7 | 25.6 | 25.9 | 24.2 | 20.1 | 14.4 | 9.9
| HP COP* | 2.6923 | 2.6084 | 2.6736 | 2.8646 | 3.1199 | 3.4192 | 3.6049 | 3.6252 | 3.5128 | 3.2683 | 2.9799 | 2.7858
| Honolulu, HI | 24.7 | 24.4 | 24.3 | 25 | 25.5 | 25.9 | 26 | 26.4 | 26.9 | 26.5 | 25.9 | 25
| HP COP* | 3.5451 | 3.5256 | 3.5192 | 3.5648 | 3.5981 | 3.6252 | 3.6321 | 3.6597 | 3.6948 | 3.6667 | 3.6252 | 3.5648
calculations:
* COP calculated is ratio of COP (actual)/COP (datacenter)* COP of manufacturer: COP = Thot/(Thot-Tcold) (actual) / COP (datacenter) * COP manufacturer
* ASHRAE D-CCC23-21.pdf
Data Center Ideal Carnot COP @ 30C:
| (273+ 79)/((273+79)- (273+24)) = 6.4 |  |  |  | 79C = Avg Hot and 24C = Avg Cold @30C DC |  |  |  | (30C+18C)/2=24C |  | COP @30C | 3.5
| Data Center Ideal Carnot COP @ 45C: | [9 empty] | COP @45C | 4.8125
| (273+ 79)/((273+79)- (273+39)) = 8.8 |  |  |  | 79C = Avg Hot and 31.5C = Avg Cold @45C DC |  |  |  | (45C+33C)/2 = 39C
Data Center Ambient Seawater COP
| (273+79)/((273+79)-(273+T)) |  |  |  | Use to calculate ambient seawater COP
352/(352-(273+T))
Actual COP is then:: COP(mfg)* COPambient (ideal carnot)/COP DC i(deal carnot)