## PFD Seawater
Microsoft 1,000 m3/Day Seawater System
Supernatant
Product
Water
Dilute
Seawater | [17 empty] | Solution
Strong Solution
Brine
Brine
[28 empty] | 30,45C In |  | 18,33C out
Data Center heat Source
System Conditions | Design Conditions
Stream Description | Feedwater | Filtered Feed | Feed Water to FO Membranes | Diluted Draw Solution | Diluted Draw to HXs | Diluted Draw to Water / Weak HX-2 | Diluted Draw and Nano Reject to HX-2 | Diluted Draw to Strong / Weak HX-1 | Warm Dilute Draw from HX-2 | Warm Dilute Draw from HX-1 | Warm Dilute Draw to Boost HX-3 | Hot Dilute Draw | Hot Water Return from Boost HX-3 | Hot Water Feed to Boost HX-3 | Hot Conc. Draw | Cooled Conc Draw | Super-natant | Cooled Super-natant | Cooling Water to HX-4 | Return Cooling Water from HX-4 | Chilled Super-natant | Pressurized Super-natant to Nanofilter | Nanofilter Permeate | Nanofilter Reject | Pressurized RO Feed | Low Pressure RO Permeate | Low Pressure RO Reject | Remineralized Product Water | FO Membrane Brine | System Brine | Chilled Strong Draw | Return Cooling Water from HX-5 | Cooling Water to HX-5 |  | Chemical Injections | Sulfuric Acid (35%) | Sodium Hypo Chlorite to Feed Water (5%) | Sodium Meta Bisulfite (10%) | Sodium Hydroxide to Weak Draw (5%) | Sodium Hydroxide to Product Water (5%) | Calcium Chloride | Sodium Hypo Chlorite to Product Water (12%) | Scale Inhibitor
Parameter | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 |  |  | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41
Temperature (deg C) | 6 - 33 | 6 - 33 | 6 - 33 | 31.8401 | 31.8401 | 31.8401 | 31.9817 | 31.8401 | 71.285 | 69.44 | 70.1559 | 85 | 80 | 90 | 85 | 37 | 85 | 41 | 25 | 32 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 31.8389 | 31.7387 | 30 | 32 | 25 |  |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Flowrate (m3/h) | 83.3333 | 83.3333 | 83.3333 | 147.2084 | 147.2084 | 55.7084 | 58.0168 | 91.5 | 58.0168 | 91.5 | 149.5168 | 149.5168 | 158.75 | 158.75 | 103.3488 | 103.3488 | 46.1681 | 46.1681 | 72.3333 | 72.3333 | 46.1681 | 46.1681 | 43.8596 | 2.3084 | 43.8596 | 41.6667 | 2.193 | 41.6667 | 39.4737 | 41.6667 | 103.3488 | 73.875 | 73.875 |  | ml/min | 166.93 | 69.21 | 785.15 | 308.78 | 54.17 | 48.37 | 10.38 | 9.64
Mass Flowrate (kg/hr) | 85412.5 | 85412.5 | 85412.5 | 157363.4288 | 157363.4288 | 59551.4199 | 61935.8904 | 97812.0089 | 61935.8904 | 97812.0089 | 159747.8993 | 159747.8993 | 153670 | 153670 | 112213.4967 | 112213.4967 | 45300.0923 | 45300.0923 | 72052.68 | 72052.68 | 45300.0923 | 45300.0923 | 43592.9825 | 1707.1099 | 43592.9825 | 41487.5 | 2105.4825 | 41487.5 | 41481.6361 | 43658.5221 | 112213.4967 | 75532.9397 | 75532.9397 |  | g/min | 198.41 | 69.44 | 810.19 | 316.67 | 55.56 | 103.99 | 10.42 | 11.55
Pressure (psi) | 30 | 27 | 27 | 5 | 23 | 23 | 23 | 23 | 19 | 19 | 19 | 15 | 3 | 5 | 15 | 10 | 15 | 13 | 5 | 3 | 11 | 110 | 5 | 23 | 105 | 10 | 10 | 5 | 10 | 10 | 6 | 3 | 5 |  |  | 27 | 27 | 27 | 5 | 5 | 5 | 5 | 27
Pressure (bar) | 2.0684 | 1.8616 | 1.8616 | 0.34474 | 1.5858 | 1.5858 | 1.5858 | 1.5858 | 1.31 | 1.31 | 1.31 | 1.0342 | 0.20684 | 0.34474 | 1.0342 | 0.68948 | 1.0342 | 0.89632 | 0.34474 | 0.20684 | 0.75842 | 7.5842 | 0.34474 | 1.5858 | 7.2395 | 0.68948 | 0.68948 | 0.34474 | 0.68948 | 0.68948 | 0.41369 | 0.20684 | 0.34474 |  |  | 1.8616 | 1.8616 | 1.8616 | 0.34474 | 0.34474 | 0.34474 | 0.34474 | 1.8616
TDS (mg/l) | 35000 | 35000 | 35000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73888.8889 | 70000 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Polymer Concentration (wt%) | 0% | 0% | 0% | 52.3% | 52.3% | 52.3% | 51.02% | 52.3% | 51.02% | 52.3% | 51.8% | 51.8% | 0% | 0% | 74.5% | 74.5% | 1% | 1% | 0% | 0% | 1% | 1% | 0% | 20% | 0% | 0% | 0% | 0% | 0% | 0% | 74.5% | 0% | 0%
pH | 7.8 | 7.8 | 6.5 | 6.5 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Heat Transfer (kW) |  |  | kWh/m3 | [5 empty] | 2318.2969 | 3528.1941 |  | 1794.0376 |  | -1794.0973 |  | -3527.8128 |  | -2318.0963 |  | 585.5721 | -585.817 | [9 empty] | -587.9688 |  | 587.8713
Supplied Heat | 1794.0973 | kW | 43.0583
Supplied Cooling | 1173.4434 | kW | 28.1626
41.6667 | m3/h | 79735.3435 | [16 empty] | 0 | [5 empty] | 0
Membrane
Draw Soln
Fresh Water
Water
Strong
Solution
Separator
Heated
Water/ Weak HX-3
Water/ Weak HX-2
Carbon / Remin.
Heat Pump
1
26
30
22
8
16
9
10
14
15
12
13
11
29
28
2
25
17
Nanofilter
6
Low Pressure RO
Filtration
3
4
5
7
27
34
35
36
37
38
39
40
41
Strong/ Weak HX-1
Supt/ Cold Water HX-4
20
18
Cooler
19
21
23
24
Cooler
Strong/ Cold Water HX-5
31
33
32