## Phoenix
Uravu and Baseline Assumptions
Facility water Return Temp (°C) | 35 | 40 | 45
Supply Temp (°C) | 23 | 28 | 33
Electricity cost ($/kWh) | 0.13 | 0.13 | 0.13
Uravu CAPEX ($) | 500000 | 500000 | 500000
Dry cooler CAPEX ($) | 150000 | 150000 | 150000
Air Cooled Chiller CAPEX ($) | 350000 | 350000 | 350000
Uravu Maintenance rate (%) | 2% | 2% | 2%
Dry cooler Maintenance rate (%) | 2% | 2% | 2%
Air Cooled chiller Maintenance rate | 3% | 3% | 3%
Amortization period (Yrs) | 15 | 15 | 15
Desgin Capacity (MW) | 10 | 10 | 10 | Can Change this number based on the desired capacity
Power Consumption per MW
Uravu elec. consumption during uptime per MW (kW/MW of cooling load) | 50 | 50 | 50
Uravu elec. consumption during downtime per MW (kW/MW of cooling load) | 40 | 40 | 40
Dry cooler elec. Consumption per MW (kW/MW of cooling load) | 45 | 45 | 45
Chiller elec. Consumption per MW (kW/MW of cooling load) | 333.3333 | 333.3333 | 333.3333 | Assuming Standard COP of 3 for Air cooled-chiller
Performance metric for Uravu - blended system
Uravu Uptime (hrs/ Yr) | 5427 | 7146 | 8573
Uravu downtime due to WBT (hrs/ Yr) | 3183 | 1470 | 3
Hours Stand-alone chiller required (hrs) | 150 | 144 | 184
Chiller Elec consumption for part load (kWh) | 1039728.6111 | 422195.2778 | 124215.2778
Chiller Elec consumption for stand-alone (kWh) | 50000 | 48000 | 61333.3333 | Chiller elec. Consumption for stand-alone = chiller elec consumption * hours stand-alone chiller required
Uravu Elec Consumption (MWh) | 14883.9861 | 8862.9528 | 6143.1861 | Uravu Elec consumption = Uravu Elec. consumption during uptime * uptime hours + Uravu elec. Consumption during downtime: downtime hours + chiller elec. Consumption for stand-alone + chiller elec consumption for part load
Gross water production (m3/MW/Yr) | 6977.5714 | 9245.5714 | 11016
Net water production (m3/MW/Yr) | 3643.1645 | 5287.1939 | 7266.8314
Baseline configuration
Hours Dry cooler sufficient | 3170 | 4483 | 5918
Hours Chiller required | 5590 | 4277 | 2842
Baseline Elec. Consumption (MWh) | 20059.8333 | 16274.0167 | 12136.4333 | Baseline Elec consumption = Hours chiller required *Chiller elec. Consumption per MW + Hours dry cooler sufficient *Dry cooler elec. Consumption per MW
Economic Analysis for the system |  |  |  | LCoC (Levelized cost of Cooling) and NVW (Net Value of Water) Formula
LCoC (Uravu-Blended) ($/MWh) | 30.8971 | 21.9618 | 17.9256 | LCoC (Uravu-blended) = (Uravu capex ammortized + Uravu maintainance + Chiller capex ammortized + Chiller maintainance + Uravu elec. Consumption * elec. Cost)/8760
LCoC (Baseline) ($/MWh) | 35.1154 | 29.4972 | 23.357 | LCoC (Baseline) = (Dry cooler capex ammortized + Dry cooler maintainance + Chiller capex ammortized + Chiller maintainance + Baseline elec. Consumption * elec. Cost)/8760
NVW (gross) ($/m3) | 13.3727 | 11.3008 | 10.3266 | NVW (gross, no credit) = (Uravu capex ammortized + Uravu maintainance + Chiller capex ammortized + Chiller maintainance + Uravu elec. consumption during uptime * uptime hours * elec. Cost)/Gross water prodcution
NVW(net) ($/m3) | 25.612 | 19.7614 | 15.6544 | NVW (net, no credit) = (Uravu capex ammortized + Uravu maintainance + Chiller capex ammortized + Chiller maintainance + Uravu elec. consumption during uptime * uptime hours * elec. Cost)/Net water prodcution
NVW( with cooling credit) ($/m3) | -10.143 | -12.485 | -6.5474 | NVW (credit) = (LCoC Uravu - LCoC baseline)/Net Water Produced
Cooling & Water-as-a-Service (CWaaS) Business Model
CWaaS discount rate on baseline LCOC (%) | 10% | 25% | 10%
Fixed Payment ammortized period | 5 | 5 | 5
Capacity payment ($/MW) ¦ Fixed payment to Uravu | 110000 | 110000 | 110000 | Capacity payment ($/MW) = covers Uravu capital recovery + minimum O&M
Usage payment ($/MWh) | 19.0468 | 9.5658 | 8.4642 | Usage payment ($/MWhcool or $/ton-hour): charged on metered delivered cooling
CWaaS charge ($/Yr) | 2768500.5 | 1937966.625 | 1841462.7 | Cooling water as a service (CWaaS) charge for a period = (1 − CWaaS dicount rate) × Baseline LCoC × (metered cooling delivered) + capacity payment
Baseline charge ($/Yr) | 3076111.6667 | 2583955.5 | 2046069.6667 | Baseline charge for a period = Baseline LCoC × metered cooling delivered
Annual Savings($/Yr) | 307611.1667 | 645988.875 | 204606.9667
Water Assest Value
Water cost ($/m3) | 2.5 | 2.5 | 2.5
Total Water Value ($/Yr) | 91079.1122 | 132179.8469 | 181670.7857 | Water Asset Value: water cost × Net water production

## Frankfurt
Uravu and Baseline Assumptions
Facility water Return Temp (°C) | 35 | 40 | 45
Supply Temp (°C) | 23 | 28 | 33
Electricity cost ($/kWh) | 0.2 | 0.2 | 0.2
Uravu CAPEX ($) | 500000 | 500000 | 500000
Dry cooler CAPEX ($) | 150000 | 150000 | 150000
Air Cooled Chiller CAPEX ($) | 350000 | 350000 | 350000
Uravu Maintenance rate (%) | 2% | 2% | 2%
Dry cooler Maintenance rate (%) | 2% | 2% | 2%
Air Cooled chiller Maintenance rate | 3% | 3% | 3%
Amortization period (Yrs) | 15 | 15 | 15
Desgin Capacity (MW) | 10 | 10 | 10 | Can Change this number based on the desired capacity
Power Consumption per MW
Uravu elec. consumption during uptime per MW (kW/MW of cooling load) | 50 | 50 | 50
Uravu elec. consumption during downtime per MW (kW/MW of cooling load) | 40 | 40 | 40
Dry cooler elec. Consumption per MW (kW/MW of cooling load) | 45 | 45 | 45
Chiller elec. Consumption per MW (kW/MW of cooling load) | 333.3333 | 333.3333 | 333.3333
Performance metric for Uravu - blended system
Uravu Uptime (hrs) | 7543 | 8618 | 8744
Uravu downtime due to WBT (hrs) | 1140 | 86 | 0
Hours Stand-alone chiller required (hrs) | 77 | 56 | 16
Chiller Elec consumption for part load (kWh) | 41038.6111 | 4860.2778 | 0
Chiller Elec consumption for stand-alone (kWh) | 25666.6667 | 18666.6667 | 5333.3333 | Chiller elec. Consumption for stand-alone = chiller elec consumption * hours stand-alone chiller required
Uravu Elec Consumption (MWh) | 4894.5528 | 4578.6694 | 4425.3333 | Uravu Elec consumption = Uravu Elec. consumption during uptime * uptime hours + Uravu elec. Consumption during downtime: downtime hours + chiller elec. Consumption for stand-alone + chiller elec consumption for part load
Gross water production (m3/MW/Yr) | 9698.1429 | 11080.2857 | 11242.2857
Net water production (m3/MW/Yr) | 8571.9037 | 10477.9886 | 11095.1486
Baseline configuration
Hours Dry cooler sufficient | 7271 | 8303 | 8678
Hours Chiller required | 1489 | 457 | 82
Baseline elec. Consumption (MWh) | 8235.2833 | 5259.6833 | 4178.4333 | Baseline Elec consumption = Hours chiller required *Chiller elec. Consumption per MW + Hours dry cooler sufficient *Dry cooler elec. Consumption per MW
Economic Analysis for the system |  |  |  | LCoC (Levelized cost of Cooling) and NVW (Net Value of Water) Formula
LCoC (Uravu-Blended) ($/MWh) | 19.9838 | 19.2626 | 18.9125 | LCoC (Uravu-blended) = (Uravu capex ammortized + Uravu maintainance + Chiller capex ammortized + Chiller maintainance + Uravu elec. Consumption * elec. Cost)/8760
LCoC (Baseline) ($/MWh) | 24.1483 | 17.3547 | 14.8861 | LCoC (Baseline) = (Dry cooler capex ammortized + Dry cooler maintainance + Chiller capex ammortized + Chiller maintainance + Baseline elec. Consumption * elec. Cost)/8760
NVW (gross) ($/m3) | 13.7617 | 13.0153 | 12.9398 | NVW (gross, no credit) = (Uravu capex ammortized + Uravu maintainance + Chiller capex ammortized + Chiller maintainance + Uravu elec. consumption during uptime * uptime hours * elec. Cost)/Gross water prodcution
NVW(net) ($/m3) | 15.5699 | 13.7635 | 13.1114 | NVW (net, no credit) = (Uravu capex ammortized + Uravu maintainance + Chiller capex ammortized + Chiller maintainance + Uravu elec. consumption during uptime * uptime hours * elec. Cost)/Net water prodcution
NVW( with cooling credit) ($/m3) | -4.2559 | 1.5951 | 3.179 | NVW (credit) = (LCoC Uravu - LCoC baseline)/Net Water Produced
Cooling & Water-as-a-Service (CWaaS) Business Model
CWaaS dicount rate (%) | 10% | 10% | 5%
Fixed Payment ammortized period | 5 | 5 | 6
Capacity payment ($/MW) ¦ Fixed payment to Uravu | 110000 | 110000 | 93333.3333 | Capacity payment ($/MW) = covers Uravu capital recovery + minimum O&M
Usage payment ($/MWh) | 9.1764 | 3.0621 | 3.4873 | Usage payment ($/MWhcool or $/ton-hour): charged on metered delivered cooling
CWaaS charge ($/Yr) | 1903851 | 1368243 | 1238819 | Cooling water as a service (CWaaS) charge for a period = (1 − CWaaS dicount rate) × Baseline LCoC × (metered cooling delivered) + capacity payment
Baseline charge ($/Yr) | 2115390 | 1520270 | 1304020 | Baseline charge for a period = Baseline LCoC × metered cooling delivered
Annual Savings($/Yr) | 211539 | 152027 | 65201
Water Assest Value
Water cost ($/m3) | 4 | 4 | 4
Total Water Value ($/Yr) | 342876.1469 | 419119.5429 | 443805.9429 | Water Asset Value: water cost × Net water production
Note on B25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reference to this assumption. How is it greater than standalone power consumption? Reply: The higher chiller energy consumption under part-load operation compared to the stand-alone system is primarily due to increased operating hours. As established earlier, the chiller’s power draw during part-load operation is lower than that of a stand-alone chiller. However, the chiller must also operate during periods of downtime (i.e., when the wet-bulb temperature exceeds the threshold). During these periods, most of the cooling demand is met by the Uravu system—operating as a dry cooler without water production—and by the indirect evaporative cooler when ambient conditions are unsuitable for dry cooling. Consequently, the extended duration of part-load operation results in higher cumulative chiller energy consumption. It is also important to note that the stand-alone chiller consumption shown in Row 25 corresponds to full-load chiller operation during periods when Uravu is unavailable due to high water usage. Therefore, the total chiller energy consumption in the Uravu-integrated case is the sum of the part-load chiller consumption and the stand-alone (full-load) consumption. Even so, when compared to the baseline chiller operation, this still represents more than an 80% reduction in chiller load. For example, total electrical consumption of chiller with Uravu = 66704 (row 25 + row 26) total baseline chiller consumption = 496328 (row 33 X row 19) total reduction = (496328 - 66704)/496328 = 86 %

## Bengaluru
Uravu and Baseline Assumptions
Facility water Return Temp (°C) | 35 | 40 | 45
Supply Temp (°C) | 23 | 28 | 33
Electricity cost ($/kWh) | 0.095 | 0.095 | 0.095
Uravu CAPEX ($) | 650000 | 500000 | 500000
Dry cooler CAPEX ($) | 150000 | 150000 | 150000
Air Cooled Chiller CAPEX ($) | 350000 | 350000 | 350000
Uravu Maintenance rate (%) | 0.02 | 0.02 | 0.02
Dry cooler Maintenance rate (%) | 0.02 | 0.02 | 0.02
Air Cooled chiller Maintenance rate | 0.03 | 0.03 | 0.03
Amortization period (Yrs) | 15 | 15 | 15
Desgin Capacity (MW) | 10 | 10 | 10 | Can Change this number based on the desired capacity
Power Consumption per MW
Uravu elec. consumption during uptime per MW (kW/MW of cooling load) | 200 | 50 | 50
Uravu elec. consumption during downtime per MW (kW/MW of cooling load) | 0 | 40 | 40
Dry cooler elec. Consumption per MW (kW/MW of cooling load) | 45 | 45 | 45
Chiller elec. Consumption per MW (kW/MW of cooling load) | 333.3333 | 333.3333 | 333.3333
Performance metric for Uravu - blended system
Uravu Uptime (hrs) | 8760 | 4859 | 8573
Uravu downtime due to WBT (hrs) | 0 | 3704 | 27
Hours Stand-alone chiller required (hrs) | 5.35 | 197 | 160
Chiller Elec consumption for part load (kWh) | 14326.7151 | 108128.3333 | 2163.8889
Chiller Elec consumption for stand-alone (kWh) | 1786.3807 | 65666.6667 | 53333.3333 | Chiller elec. Consumption for stand-alone = chiller elec consumption * hours stand-alone chiller required
Uravu Elec Consumption (MWh) | 17681.131 | 5649.05 | 4852.2722 | Uravu Elec consumption = Uravu Elec. consumption during uptime * uptime hours + Uravu elec. Consumption during downtime: downtime hours + chiller elec. Consumption for stand-alone + chiller elec consumption for part load
Gross water production (m3/MW/Yr) | 14038.4615 | 6247.2857 | 11022.4286
Net water production (m3/MW/Yr) | 12391.9033 | 3205.9004 | 8929.7792
Baseline configuration
Hours Dry cooler sufficient | 427 | 4232 | 7534
Hours Chiller required | 8333 | 4528 | 1226
Baseline elec. Consumption (MWh) | 27968.8167 | 16997.7333 | 7476.9667 | Baseline Elec consumption = Hours chiller required *Chiller elec. Consumption per MW + Hours dry cooler sufficient *Dry cooler elec. Consumption per MW
Economic Analysis for the system |  |  |  | LCoC (Levelized cost of Cooling) and NVW (Net Value of Water) Formula
LCoC (Uravu-Blended) ($/MWh) | 29.4677 | 14.9352 | 14.0711 | LCoC (Uravu-blended) = (Uravu capex ammortized + Uravu maintainance + Chiller capex ammortized + Chiller maintainance + Uravu elec. Consumption * elec. Cost)/8760
LCoC (Baseline) ($/MWh) | 35.6778 | 23.7799 | 13.4549 | LCoC (Baseline) = (Dry cooler capex ammortized + Dry cooler maintainance + Chiller capex ammortized + Chiller maintainance + Baseline elec. Consumption * elec. Cost)/8760
NVW (gross) ($/m3) | 16.7165 | 12.9838 | 8.9595 | NVW (gross, no credit) = (Uravu capex ammortized + Uravu maintainance + Chiller capex ammortized + Chiller maintainance + Uravu elec. consumption during uptime * uptime hours * elec. Cost)/Gross water prodcution
NVW(net) ($/m3) | 18.9376 | 25.3013 | 11.0591 | NVW (net, no credit) = (Uravu capex ammortized + Uravu maintainance + Chiller capex ammortized + Chiller maintainance + Uravu elec. consumption during uptime * uptime hours * elec. Cost)/Net water prodcution
NVW( with cooling credit) ($/m3) | -4.3899 | -24.1677 | 0.60458 | NVW (credit) = (LCoC Uravu - LCoC baseline)/Net Water Produced
Cooling & Water-as-a-Service (CWaaS) Business Model
CWaaS discount rate on baseline LCOC (%) | 10% | 15% | 5%
Fixed Payment ammortized period | 5 | 5 | 6
Capacity payment ($/MW) ¦ Fixed payment to Uravu | 110000 | 110000 | 93333.3333 | Capacity payment ($/MW) = covers Uravu capital recovery + minimum O&M
Usage payment ($/MWh) | 19.5529 | 7.6558 | 2.1276 | Usage payment ($/MWhcool or $/ton-hour): charged on metered delivered cooling
CWaaS charge ($/Yr) | 2812833.825 | 1770650.3 | 1119712.9083 | Cooling water as a service (CWaaS) charge for a period = (1 − CWaaS dicount rate) × Baseline LCoC × (metered cooling delivered) + capacity payment
Baseline charge ($/Yr) | 3125370.9167 | 2083118 | 1178645.1667 | Baseline charge for a period = Baseline LCoC × metered cooling delivered
Annual Savings($/Yr) | 312537.0917 | 312467.7 | 58932.2583
Water Assest Value
Water cost ($/m3) | 2 | 2 | 2
Total Water Value ($/Yr) | 247838.0659 | 64118.0082 | 178595.5837 | Water Asset Value: water cost × Net water production