## Phoenix
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-electric system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13
CAPEX ($) | 600000 | 600000 | 600000 | 600000 | 600000 | 600000 | 600000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 100 | 100 | 100 | 100 | 100 | 100 | 100
Rated Power (Normal Operation) (kW) | 20 | 20 | 20 | 20 | 20 | 20 | 20
Uravu electrical consumption (kWh) | 175200 | 175200 | 175200 | 175200 | 175200 | 175200 | 175200
Waste heat Utulization (hr) | 5902 | 7347 | 8283 | 8708 | 8760 | 8760 | 8760
Waste heat downtime (hr) | 2858 | 1413 | 477 | 52 | 0 | 0 | 0
Chiller required with waste heat (hr) | 322 | 20 | 0 | 0 | 0 | 0 | 0
Chiller requried without waste heat utulization (hr) | 1714 | 97 | 0 | 0 | 0 | 0 | 0
Fraction of time chiller is required (%) | 23.242 | 1.3356 | 0 | 0 | 0 | 0 | 0
Reduction in Chiller heat load (%) | 93.0354 | 99.8458 | 100 | 100 | 100 | 100 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615
Water used for cooling in when waste heat is utlized (m³/MW/year) | 1535.3044 | 1732.3853 | 1197.8371 | 570.5004 | 96.0224 | 1.759 | 0
Water used for cooling when waste heat is not utilized (m³/MW/year) | 3424.9539 | 2059.6882 | 700.898 | 76.4082 | 0 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 9078.2032 | 10246.3881 | 12139.7265 | 13391.553 | 13942.4392 | 14036.7025 | 14038.4615
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 1742 | 3170 | 4483 | 5918 | 7351 | 8285 | 8709
Hours Air-cooled Chiller Required | 7018 | 5590 | 4277 | 2842 | 1409 | 475 | 51
Electricity Cost ($) | 314304.0333 | 260777.8333 | 211562.2167 | 157773.6333 | 104060.0167 | 69050.5833 | 53157.65
Fixed Costs (Dynamic CAPEX/Maint)($) | 42500 | 42500 | 42500 | 42500 | 42500 | 42500 | 42500
Total annualized cost (Uravu + air cooled chiller ($/MW) | 341680.5587 | 314215.0479 | 313593.3333 | 313593.3333 | 313593.3333 | 313593.3333 | 313593.3333
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 356804.0333 | 303277.8333 | 254062.2167 | 200273.6333 | 146560.0167 | 111550.5833 | 95657.65
Total avoided cost (Air-cooled chiller($/MW)) | 413433.3333 | 413433.3333 | 413433.3333 | 413433.3333 | 413433.3333 | 413433.3333 | 413433.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 279760 | 279760 | 279760 | 279760 | 279760 | 279760 | 279760
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | -77044.0333 | -23517.8333 | 25697.7833 | 79486.3667 | 133199.9833 | 168209.4167 | 184102.35
Net cost allocated to water (Air-cooled chiller) | -71752.7746 | -99218.2854 | -99840 | -99840 | -99840 | -99840 | -99840
LCOW (Gross Production) | 19.9281 | 19.9281 | 19.9281 | 19.9281 | 19.9281 | 19.9281 | 19.9281
LCOW (Net Delivered, No Credit) | 26.3589 | 23.3546 | 20.9753 | 20.0372 | 19.9281 | 19.9281 | 19.9281
Fair LCOW (Dry cooler + Air cooled chiller) | -1.4249 | 0.91305 | 4.4634 | 8.1163 | 11.8983 | 14.3921 | 15.5242
Fair LCOW (Air cooled chiller) | -6.7605 | -8.2828 | -7.4856 | -7.1508 | -7.1119 | -7.1119 | -7.1119
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 1968055.58 | 1756782.42 | 1752000 | 1752000 | 1752000 | 1752000 | 1752000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 2417723.3333 | 2005983.3333 | 1627401.6667 | 1213643.3333 | 800461.6667 | 531158.3333 | 408905
PUE_uravu | 1.2247 | 1.2005 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.276 | 1.229 | 1.1858 | 1.1385 | 1.0914 | 1.0606 | 1.0467
WUE | -1.2116 | -1.3674 | -1.5226 | -1.5938 | -1.6026 | -1.6026 | -1.6026
Grid CO₂ (kg/kWh) | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
Grid water (L/kWh) | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Uravu water foot print (m3/year) | 5438.9688 | 3824.2361 | 2572.0938 | 1518.8715 | 1236.1458 | 1137.0521 | 1102.0833
Uravu CO2 emission (tCO₂/yr) | 979.0144 | 688.3625 | 462.9769 | 273.3969 | 222.5063 | 204.6694 | 198.375

## Chicago
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-electric system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
CAPEX ($) | 650000 | 650000 | 650000 | 650000 | 650000 | 650000 | 650000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 100 | 100 | 100 | 100 | 100 | 100 | 100
Rated Power (Normal Operation) (kW) | 20 | 20 | 20 | 20 | 20 | 20 | 20
Uravu electrical consumption (kWh) | 175200 | 175200 | 175200 | 175200 | 175200 | 175200 | 175200
Waste heat Utulization (hr) | 8499 | 8742 | 8760 | 8760 | 8760 | 8760 | 8760
Waste heat downtime (hr) | 261 | 18 | 0 | 0 | 0 | 0 | 0
Chiller required with waste heat (hr) | 1342 | 283 | 1 | 0 | 0 | 0 | 0
Chiller requried without waste heat utulization (hr) | 260 | 18 | 0 | 0 | 0 | 0 | 0
Fraction of time chiller is required (%) | 18.2877 | 3.4361 | 0.011416 | 0 | 0 | 0 | 0
Reduction in Chiller heat load (%) | 94.0639 | 99.3811 | 99.9982 | 100 | 100 | 100 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615
Water used for cooling in when waste heat is utlized (m³/MW/year) | 810.11 | 263.8588 | 39.9786 | 0.22606 | 0 | 0 | 0
Water used for cooling when waste heat is not utilized (m³/MW/year) | 188.328 | 18.8293 | 0 | 0 | 0 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 13040.0235 | 13755.7734 | 13998.483 | 14038.2355 | 14038.4615 | 14038.4615 | 14038.4615
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 5011 | 6060 | 7505 | 8502 | 8742 | 8760 | 8760
Hours Air-cooled Chiller Required | 3749 | 2700 | 1255 | 258 | 18 | 0 | 0
Electricity Cost ($) | 177019.4 | 140724 | 90727 | 56230.8 | 47926.8 | 47304 | 47304
Fixed Costs (Dynamic CAPEX/Maint)($) | 42500 | 42500 | 42500 | 42500 | 42500 | 8666.6667 | 8666.6667
Total annualized cost (Uravu + air cooled chiller ($/MW) | 322504.7294 | 302710.602 | 300413.2429 | 300406.6667 | 300406.6667 | 300406.6667 | 300406.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 219519.4 | 183224 | 133227 | 98730.8 | 90426.8 | 55970.6667 | 55970.6667
Total avoided cost (Air-cooled chiller($/MW)) | 384233.3333 | 384233.3333 | 384233.3333 | 384233.3333 | 384233.3333 | 384233.3333 | 384233.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 266573.3333 | 266573.3333 | 266573.3333 | 266573.3333 | 266573.3333 | 266573.3333 | 266573.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | 47053.9333 | 83349.3333 | 133346.3333 | 167842.5333 | 176146.5333 | 210602.6667 | 210602.6667
Net cost allocated to water (Air-cooled chiller) | -61728.604 | -81522.7313 | -83820.0904 | -83826.6667 | -83826.6667 | -83826.6667 | -83826.6667
LCOW (Gross Production) | 18.9888 | 18.9888 | 18.9888 | 18.9888 | 18.9888 | 18.9888 | 18.9888
LCOW (Net Delivered, No Credit) | 19.247 | 19.0143 | 18.9888 | 18.9888 | 18.9888 | 18.9888 | 18.9888
Fair LCOW (Dry cooler + Air cooled chiller) | 7.4357 | 8.5228 | 11.9092 | 14.366 | 14.9575 | 17.4119 | 17.4119
Fair LCOW (Air cooled chiller) | -4.4569 | -5.8149 | -5.9707 | -5.9712 | -5.9712 | -5.9712 | -5.9712
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 1936150.5225 | 1771199.4612 | 1752054.8021 | 1752000 | 1752000 | 1752000 | 1752000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 1475161.6667 | 1172700 | 756058.3333 | 468590 | 399390 | 394200 | 394200
PUE_uravu | 1.221 | 1.2022 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.1684 | 1.1339 | 1.0863 | 1.0535 | 1.0456 | 1.045 | 1.045
WUE | -1.5811 | -1.6004 | -1.6026 | -1.6026 | -1.6026 | -1.6026 | -1.6026
Grid CO₂ (kg/kWh) | 0.334 | 0.334 | 0.334 | 0.334 | 0.334 | 0.334 | 0.334
Grid water (L/kWh) | 3.97 | 3.97 | 3.97 | 3.97 | 3.97 | 3.97 | 3.97
Uravu water foot print (m3/year) | 7686.5176 | 7031.6619 | 6955.6576 | 6955.44 | 6955.44 | 6955.44 | 6955.44
Uravu CO2 emission (tCO₂/yr) | 646.6743 | 591.5806 | 585.1863 | 585.168 | 585.168 | 585.168 | 585.168

## Houston
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-electric system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11
CAPEX ($) | 650000 | 650000 | 650000 | 650000 | 650000 | 650000 | 650000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 100 | 100 | 100 | 100 | 100 | 100 | 100
Rated Power (Normal Operation) (kW) | 20 | 20 | 20 | 20 | 20 | 20 | 20
Uravu electrical consumption (kWh) | 175200 | 175200 | 175200 | 175200 | 175200 | 175200 | 175200
Waste heat Utulization (hr) | 6778 | 8153 | 8724 | 8760 | 8760 | 8760 | 8760
Waste heat downtime (hr) | 1982 | 607 | 36 | 0 | 0 | 0 | 0
Chiller required with waste heat (hr) | 2948 | 1739 | 55 | 0 | 0 | 0 | 0
Chiller requried without waste heat utulization (hr) | 1948 | 531 | 7 | 0 | 0 | 0 | 0
Fraction of time chiller is required (%) | 55.8904 | 25.9132 | 0.70776 | 0 | 0 | 0 | 0
Reduction in Chiller heat load (%) | 73.3712 | 94.133 | 99.8821 | 100 | 100 | 100 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615
Water used for cooling in when waste heat is utlized (m³/MW/year) | 2076.8087 | 1068.917 | 584.6233 | 69.7995 | 1.5754 | 0 | 0
Water used for cooling when waste heat is not utilized (m³/MW/year) | 1222.4248 | 671.6313 | 50.7426 | 0 | 0 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 10739.228 | 12297.9132 | 13403.0956 | 13968.6621 | 14036.8862 | 14038.4615 | 14038.4615
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 1456 | 2743 | 4692 | 7117 | 8344 | 8751 | 8760
Hours Air-cooled Chiller Required | 7304 | 6017 | 4068 | 1643 | 416 | 9 | 0
Electricity Cost ($) | 275020.5333 | 234201.1833 | 172385.4 | 95472.4833 | 56556.1333 | 43647.45 | 43362
Fixed Costs (Dynamic CAPEX/Maint)($) | 42500 | 42500 | 42500 | 42500 | 42500 | 42500 | 8666.6667
Total annualized cost (Uravu + air cooled chiller ($/MW) | 373755.6902 | 302907.3056 | 283288.9051 | 282886.6667 | 282886.6667 | 282886.6667 | 282886.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 317520.5333 | 276701.1833 | 214885.4 | 137972.4833 | 99056.1333 | 86147.45 | 52028.6667
Total avoided cost (Air-cooled chiller($/MW)) | 355033.3333 | 355033.3333 | 355033.3333 | 355033.3333 | 355033.3333 | 355033.3333 | 355033.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 249053.3333 | 249053.3333 | 249053.3333 | 249053.3333 | 249053.3333 | 249053.3333 | 249053.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | -68467.2 | -27647.85 | 34167.9333 | 111080.85 | 149997.2 | 162905.8833 | 197024.6667
Net cost allocated to water (Air-cooled chiller) | 18722.3568 | -52126.0277 | -71744.4283 | -72146.6667 | -72146.6667 | -72146.6667 | -72146.6667
LCOW (Gross Production) | 17.7408 | 17.7408 | 17.7408 | 17.7408 | 17.7408 | 17.7408 | 17.7408
LCOW (Net Delivered, No Credit) | 19.4329 | 18.6322 | 17.8051 | 17.7408 | 17.7408 | 17.7408 | 17.7408
Fair LCOW (Dry cooler + Air cooled chiller) | 4.3879 | 1.9605 | 4.8903 | 10.3227 | 13.0948 | 14.0143 | 16.4447
Fair LCOW (Air cooled chiller) | 1.4609 | -3.8997 | -5.1291 | -5.1392 | -5.1392 | -5.1392 | -5.1392
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 2578082.0317 | 1934005.8086 | 1755656.7127 | 1752000 | 1752000 | 1752000 | 1752000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 2500186.6667 | 2129101.6667 | 1567140 | 867931.6667 | 514146.6667 | 396795 | 394200
PUE_uravu | 1.2943 | 1.2208 | 1.2004 | 1.2 | 1.2 | 1.2 | 1.2
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.2854 | 1.243 | 1.1789 | 1.0991 | 1.0587 | 1.0453 | 1.045
WUE | -1.463 | -1.5259 | -1.5968 | -1.6026 | -1.6026 | -1.6026 | -1.6026
Grid CO₂ (kg/kWh) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Grid water (L/kWh) | 3 | 3 | 3 | 3 | 3 | 3 | 3
Uravu water foot print (m3/year) | 7734.2461 | 5802.0174 | 5266.9701 | 5256 | 5256 | 5256 | 5256
Uravu CO2 emission (tCO₂/yr) | 1289.041 | 967.0029 | 877.8284 | 876 | 876 | 876 | 876

## Seattle
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-electric system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
CAPEX ($) | 650000 | 650000 | 650000 | 650000 | 650000 | 650000 | 650000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 100 | 100 | 100 | 100 | 100 | 100 | 100
Rated Power (Normal Operation) (kW) | 20 | 20 | 20 | 20 | 20 | 20 | 20
Uravu electrical consumption (kWh) | 175200 | 175200 | 175200 | 175200 | 175200 | 175200 | 175200
Waste heat Utulization (hr) | 8744 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
Waste heat downtime (hr) | 16 | 0 | 0 | 0 | 0 | 0 | 0
Chiller required with waste heat (hr) | 95 | 0 | 0 | 0 | 0 | 0 | 0
Chiller requried without waste heat utulization (hr) | 16 | 0 | 0 | 0 | 0 | 0 | 0
Fraction of time chiller is required (%) | 1.2671 | 0 | 0 | 0 | 0 | 0 | 0
Reduction in Chiller heat load (%) | 99.782 | 100 | 100 | 100 | 100 | 100 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615
Water used for cooling in when waste heat is utlized (m³/MW/year) | 199.1568 | 33.1743 | 0.44152 | 0 | 0 | 0 | 0
Water used for cooling when waste heat is not utilized (m³/MW/year) | 18.1115 | 0 | 0 | 0 | 0 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 13821.1932 | 14005.2873 | 14038.02 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 5289 | 7818 | 8564 | 8745 | 8760 | 8760 | 8760
Hours Air-cooled Chiller Required | 3471 | 942 | 196 | 15 | 0 | 0 | 0
Electricity Cost ($) | 139500.5 | 66581 | 45071.3333 | 39852.5 | 39420 | 39420 | 39420
Fixed Costs (Dynamic CAPEX/Maint)($) | 42500 | 42500 | 42500 | 42500 | 8666.6667 | 8666.6667 | 8666.6667
Total annualized cost (Uravu + air cooled chiller ($/MW) | 266042.8349 | 265366.6667 | 265366.6667 | 265366.6667 | 265366.6667 | 265366.6667 | 265366.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 182000.5 | 109081 | 87571.3333 | 82352.5 | 48086.6667 | 48086.6667 | 48086.6667
Total avoided cost (Air-cooled chiller($/MW)) | 325833.3333 | 325833.3333 | 325833.3333 | 325833.3333 | 325833.3333 | 325833.3333 | 325833.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 231533.3333 | 231533.3333 | 231533.3333 | 231533.3333 | 231533.3333 | 231533.3333 | 231533.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | 49532.8333 | 122452.3333 | 143962 | 149180.8333 | 183446.6667 | 183446.6667 | 183446.6667
Net cost allocated to water (Air-cooled chiller) | -59790.4984 | -60466.6667 | -60466.6667 | -60466.6667 | -60466.6667 | -60466.6667 | -60466.6667
LCOW (Gross Production) | 16.4928 | 16.4928 | 16.4928 | 16.4928 | 16.4928 | 16.4928 | 16.4928
LCOW (Net Delivered, No Credit) | 16.5141 | 16.4928 | 16.4928 | 16.4928 | 16.4928 | 16.4928 | 16.4928
Fair LCOW (Dry cooler + Air cooled chiller) | 5.9943 | 11.1327 | 12.6649 | 13.0366 | 15.4775 | 15.4775 | 15.4775
Fair LCOW (Air cooled chiller) | -4.2646 | -4.3072 | -4.3072 | -4.3072 | -4.3072 | -4.3072 | -4.3072
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 1758761.6827 | 1752000 | 1752000 | 1752000 | 1752000 | 1752000 | 1752000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 1395005 | 665810 | 450713.3333 | 398525 | 394200 | 394200 | 394200
PUE_uravu | 1.2008 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.1592 | 1.076 | 1.0515 | 1.0455 | 1.045 | 1.045 | 1.045
WUE | -1.6005 | -1.6026 | -1.6026 | -1.6026 | -1.6026 | -1.6026 | -1.6026
Grid CO₂ (kg/kWh) | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
Grid water (L/kWh) | 1 | 1 | 1 | 1 | 1 | 1 | 1
Uravu water foot print (m3/year) | 1758.7617 | 1752 | 1752 | 1752 | 1752 | 1752 | 1752
Uravu CO2 emission (tCO₂/yr) | 35.1752 | 35.04 | 35.04 | 35.04 | 35.04 | 35.04 | 35.04

## Frankfurt
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-electric system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
CAPEX ($) | 650000 | 650000 | 650000 | 650000 | 650000 | 650000 | 650000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 100 | 100 | 100 | 100 | 100 | 100 | 100
Rated Power (Normal Operation) (kW) | 20 | 20 | 20 | 20 | 20 | 20 | 20
Uravu electrical consumption (kWh) | 175200 | 175200 | 175200 | 175200 | 175200 | 175200 | 175200
Waste heat Utulization (hr) | 8672 | 8758 | 8760 | 8760 | 8760 | 8760 | 8760
Waste heat downtime (hr) | 88 | 2 | 0 | 0 | 0 | 0 | 0
Chiller required with waste heat (hr) | 207 | 0 | 0 | 0 | 0 | 0 | 0
Chiller requried without waste heat utulization (hr) | 74 | 0 | 0 | 0 | 0 | 0 | 0
Fraction of time chiller is required (%) | 3.2078 | 0 | 0 | 0 | 0 | 0 | 0
Reduction in Chiller heat load (%) | 99.3732 | 100 | 100 | 100 | 100 | 100 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615
Water used for cooling in when waste heat is utlized (m³/MW/year) | 382.3187 | 113.3795 | 7.248 | 0 | 0 | 0 | 0
Water used for cooling when waste heat is not utilized (m³/MW/year) | 102.4788 | 2.9388 | 0 | 0 | 0 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 13553.6641 | 13922.1432 | 14031.2135 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 14 | 19 | 24 | 29 | 34 | 39 | 44
Hours Dry Cooler is Sufficient | 7212 | 8598 | 8760 | 8760 | 8760 | 8760 | 8760
Hours Air-cooled Chiller Required | 1548 | 162 | 0 | 0 | 0 | 0 | 0
Electricity Cost ($) | 117624 | 27996 | 17520 | 17520 | 17520 | 17520 | 17520
Fixed Costs (Dynamic CAPEX/Maint)($) | 36866.6667 | 36866.6667 | 3033.3333 | 3033.3333 | 3033.3333 | 3033.3333 | 3033.3333
Total annualized cost (Uravu + air cooled chiller ($/MW) | 444455.6291 | 440566.6667 | 440566.6667 | 440566.6667 | 440566.6667 | 440566.6667 | 440566.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 281421.8667 | 216187.4667 | 174729.3333 | 174729.3333 | 174729.3333 | 174729.3333 | 174729.3333
Total avoided cost (Air-cooled chiller($/MW)) | 617833.3333 | 617833.3333 | 617833.3333 | 617833.3333 | 617833.3333 | 617833.3333 | 617833.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 406733.3333 | 406733.3333 | 406733.3333 | 406733.3333 | 406733.3333 | 406733.3333 | 406733.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | 125311.4667 | 190545.8667 | 232004 | 232004 | 232004 | 232004 | 232004
Net cost allocated to water (Air-cooled chiller) | -173377.7042 | -177266.6667 | -177266.6667 | -177266.6667 | -177266.6667 | -177266.6667 | -177266.6667
LCOW (Gross Production) | 28.9728 | 28.9728 | 28.9728 | 28.9728 | 28.9728 | 28.9728 | 28.9728
LCOW (Net Delivered, No Credit) | 29.1858 | 28.9789 | 28.9728 | 28.9728 | 28.9728 | 28.9728 | 28.9728
Fair LCOW (Dry cooler + Air cooled chiller) | 11.6988 | 15.9865 | 18.9364 | 18.9364 | 18.9364 | 18.9364 | 18.9364
Fair LCOW (Air cooled chiller) | -12.441 | -12.6299 | -12.6272 | -12.6272 | -12.6272 | -12.6272 | -12.6272
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 1968055.58 | 1756782.42 | 1752000 | 1752000 | 1752000 | 1752000 | 1752000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 2417723.3333 | 2005983.3333 | 1627401.6667 | 1213643.3333 | 800461.6667 | 531158.3333 | 408905
PUE_uravu | 1.2022 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.276 | 1.229 | 1.1858 | 1.1385 | 1.0914 | 1.0606 | 1.0467
WUE | -1.5909 | -1.6022 | -1.6026 | -1.6026 | -1.6026 | -1.6026 | -1.6026
Grid CO₂ (kg/kWh) | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
Grid water (L/kWh) | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Uravu water foot print (m3/year) | 4920.139 | 4391.9561 | 4380 | 4380 | 4380 | 4380 | 4380
Uravu CO2 emission (tCO₂/yr) | 688.8195 | 614.8738 | 613.2 | 613.2 | 613.2 | 613.2 | 613.2

## Madrid
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-electric system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
CAPEX ($) | 650000 | 650000 | 650000 | 650000 | 650000 | 650000 | 650000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 100 | 100 | 100 | 100 | 100 | 100 | 100
Rated Power (Normal Operation) (kW) | 20 | 20 | 20 | 20 | 20 | 20 | 20
Uravu electrical consumption (kWh) | 175200 | 175200 | 175200 | 175200 | 175200 | 175200 | 175200
Waste heat Utulization (hr) | 7937 | 8526 | 8747 | 8760 | 8760 | 8760 | 8760
Waste heat downtime (hr) | 823 | 234 | 13 | 0 | 0 | 0 | 0
Chiller required with waste heat (hr) | 54 | 0 | 0 | 0 | 0 | 0 | 0
Chiller requried without waste heat utulization (hr) | 380 | 0 | 0 | 0 | 0 | 0 | 0
Fraction of time chiller is required (%) | 4.9543 | 0 | 0 | 0 | 0 | 0 | 0
Reduction in Chiller heat load (%) | 99.1344 | 100 | 100 | 100 | 100 | 100 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615
Water used for cooling in when waste heat is utlized (m³/MW/year) | 981.0568 | 726.531 | 307.9144 | 33.1884 | 0 | 0 | 0
Water used for cooling when waste heat is not utilized (m³/MW/year) | 1109.7125 | 343.8367 | 19.102 | 0 | 0 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 11947.6922 | 12968.0938 | 13711.4451 | 14005.2732 | 14038.4615 | 14038.4615 | 14038.4615
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 4077 | 5842 | 7143 | 7953 | 8539 | 8751 | 8760
Hours Air-cooled Chiller Required | 4683 | 2918 | 1617 | 807 | 221 | 9 | 0
Electricity Cost ($) | 314003.7 | 222400.2 | 154878.3 | 112839.3 | 82425.9 | 71423.1 | 70956
Fixed Costs (Dynamic CAPEX/Maint)($) | 42500 | 42500 | 42500 | 42500 | 42500 | 42500 | 8666.6667
Total annualized cost (Uravu + air cooled chiller ($/MW) | 410360.0473 | 405526.6667 | 405526.6667 | 405526.6667 | 405526.6667 | 405526.6667 | 405526.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 356503.7 | 264900.2 | 197378.3 | 155339.3 | 124925.9 | 113923.1 | 79622.6667
Total avoided cost (Air-cooled chiller($/MW)) | 559433.3333 | 559433.3333 | 559433.3333 | 559433.3333 | 559433.3333 | 559433.3333 | 559433.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 371693.3333 | 371693.3333 | 371693.3333 | 371693.3333 | 371693.3333 | 371693.3333 | 371693.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | 15189.6333 | 106793.1333 | 174315.0333 | 216354.0333 | 246767.4333 | 257770.2333 | 292070.6667
Net cost allocated to water (Air-cooled chiller) | -149073.286 | -153906.6667 | -153906.6667 | -153906.6667 | -153906.6667 | -153906.6667 | -153906.6667
LCOW (Gross Production) | 26.4768 | 26.4768 | 26.4768 | 26.4768 | 26.4768 | 26.4768 | 26.4768
LCOW (Net Delivered, No Credit) | 28.7494 | 27.1415 | 26.5129 | 26.4768 | 26.4768 | 26.4768 | 26.4768
Fair LCOW (Dry cooler + Air cooled chiller) | 4.1656 | 10.2687 | 14.8472 | 17.8216 | 19.988 | 20.7718 | 23.2151
Fair LCOW (Air cooled chiller) | -11.5304 | -11.2385 | -10.9782 | -10.9632 | -10.9632 | -10.9632 | -10.9632
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 1778852.1148 | 1752000 | 1752000 | 1752000 | 1752000 | 1752000 | 1752000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 1744465 | 1235556.6667 | 860435 | 626885 | 457921.6667 | 396795 | 394200
PUE_uravu | 1.2031 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.1991 | 1.141 | 1.0982 | 1.0716 | 1.0523 | 1.0453 | 1.045
WUE | -1.4759 | -1.5633 | -1.6004 | -1.6026 | -1.6026 | -1.6026 | -1.6026
Grid CO₂ (kg/kWh) | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108
Grid water (L/kWh) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8
Uravu water foot print (m3/year) | 3201.9338 | 3153.6 | 3153.6 | 3153.6 | 3153.6 | 3153.6 | 3153.6
Uravu CO2 emission (tCO₂/yr) | 192.116 | 189.216 | 189.216 | 189.216 | 189.216 | 189.216 | 189.216

## London
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-electric system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
CAPEX ($) | 650000 | 650000 | 650000 | 650000 | 650000 | 650000 | 650000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 100 | 100 | 100 | 100 | 100 | 100 | 100
Rated Power (Normal Operation) (kW) | 20 | 20 | 20 | 20 | 20 | 20 | 20
Uravu electrical consumption (kWh) | 175200 | 175200 | 175200 | 175200 | 175200 | 175200 | 175200
Waste heat Utulization (hr) | 8742 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
Waste heat downtime (hr) | 18 | 0 | 0 | 0 | 0 | 0 | 0
Chiller required with waste heat (hr) | 212 | 1 | 0 | 0 | 0 | 0 | 0
Chiller requried without waste heat utulization (hr) | 14 | 0 | 0 | 0 | 0 | 0 | 0
Fraction of time chiller is required (%) | 2.5799 | 0.011416 | 0 | 0 | 0 | 0 | 0
Reduction in Chiller heat load (%) | 99.5294 | 99.9988 | 100 | 100 | 100 | 100 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615
Water used for cooling in when waste heat is utlized (m³/MW/year) | 166.0243 | 25.2905 | 0.69937 | 0 | 0 | 0 | 0
Water used for cooling when waste heat is not utilized (m³/MW/year) | 19.5101 | 0 | 0 | 0 | 0 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 13852.9271 | 14013.1711 | 14037.7622 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 6359 | 8039 | 8595 | 8752 | 8760 | 8760 | 8760
Hours Air-cooled Chiller Required | 2401 | 721 | 165 | 8 | 0 | 0 | 0
Electricity Cost ($) | 217297.6667 | 120417.6667 | 88355 | 79301.3333 | 78840 | 78840 | 78840
Fixed Costs (Dynamic CAPEX/Maint)($) | 42500 | 42500 | 42500 | 42500 | 8666.6667 | 8666.6667 | 8666.6667
Total annualized cost (Uravu + air cooled chiller ($/MW) | 443486.3601 | 440573.819 | 440566.6667 | 440566.6667 | 440566.6667 | 440566.6667 | 440566.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 259797.6667 | 162917.6667 | 130855 | 121801.3333 | 87506.6667 | 87506.6667 | 87506.6667
Total avoided cost (Air-cooled chiller($/MW)) | 617833.3333 | 617833.3333 | 617833.3333 | 617833.3333 | 617833.3333 | 617833.3333 | 617833.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 406733.3333 | 406733.3333 | 406733.3333 | 406733.3333 | 406733.3333 | 406733.3333 | 406733.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | 146935.6667 | 243815.6667 | 275878.3333 | 284932 | 319226.6667 | 319226.6667 | 319226.6667
Net cost allocated to water (Air-cooled chiller) | -174346.9732 | -177259.5143 | -177266.6667 | -177266.6667 | -177266.6667 | -177266.6667 | -177266.6667
LCOW (Gross Production) | 28.9728 | 28.9728 | 28.9728 | 28.9728 | 28.9728 | 28.9728 | 28.9728
LCOW (Net Delivered, No Credit) | 29.0131 | 28.9728 | 28.9728 | 28.9728 | 28.9728 | 28.9728 | 28.9728
Fair LCOW (Dry cooler + Air cooled chiller) | 13.1029 | 19.7782 | 22.0617 | 22.7066 | 25.1495 | 25.1495 | 25.1495
Fair LCOW (Air cooled chiller) | -12.4365 | -12.6267 | -12.6272 | -12.6272 | -12.6272 | -12.6272 | -12.6272
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 1766598.4673 | 1752035.7619 | 1752000 | 1752000 | 1752000 | 1752000 | 1752000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 1086488.3333 | 602088.3333 | 441775 | 396506.6667 | 394200 | 394200 | 394200
PUE_uravu | 1.2017 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.124 | 1.0687 | 1.0504 | 1.0453 | 1.045 | 1.045 | 1.045
WUE | -1.6003 | -1.6026 | -1.6026 | -1.6026 | -1.6026 | -1.6026 | -1.6026
Grid CO₂ (kg/kWh) | 0.19 | 0.19 | 0.19 | 0.19 | 0.19 | 0.19 | 0.19
Grid water (L/kWh) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
Uravu water foot print (m3/year) | 2649.8977 | 2628.0536 | 2628 | 2628 | 2628 | 2628 | 2628
Uravu CO2 emission (tCO₂/yr) | 335.6537 | 332.8868 | 332.88 | 332.88 | 332.88 | 332.88 | 332.88

## Stockholm
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-electric system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
CAPEX ($) | 650000 | 650000 | 650000 | 650000 | 650000 | 650000 | 650000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 100 | 100 | 100 | 100 | 100 | 100 | 100
Rated Power (Normal Operation) (kW) | 20 | 20 | 20 | 20 | 20 | 20 | 20
Uravu electrical consumption (kWh) | 175200 | 175200 | 175200 | 175200 | 175200 | 175200 | 175200
Waste heat Utulization (hr) | 8725 | 8757 | 8760 | 8760 | 8760 | 8760 | 8760
Waste heat downtime (hr) | 35 | 3 | 0 | 0 | 0 | 0 | 0
Chiller required with waste heat (hr) | 157 | 0 | 0 | 0 | 0 | 0 | 0
Chiller requried without waste heat utulization (hr) | 31 | 3 | 0 | 0 | 0 | 0 | 0
Fraction of time chiller is required (%) | 2.1461 | 0.034247 | 0 | 0 | 0 | 0 | 0
Reduction in Chiller heat load (%) | 99.5289 | 99.9948 | 100 | 100 | 100 | 100 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615
Water used for cooling in when waste heat is utlized (m³/MW/year) | 234.2628 | 52.9686 | 3.5286 | 0 | 0 | 0 | 0
Water used for cooling when waste heat is not utilized (m³/MW/year) | 36.2881 | 3.7364 | 0 | 0 | 0 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 13767.9106 | 13981.7565 | 14034.9329 | 14038.4615 | 14038.4615 | 14038.4615 | 14038.4615
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 6187 | 7744 | 8521 | 8728 | 8757 | 8760 | 8760
Hours Air-cooled Chiller Required | 2573 | 1016 | 239 | 32 | 3 | 0 | 0
Electricity Cost ($) | 170412.25 | 103072 | 69466.75 | 60514 | 59259.75 | 59130 | 59130
Fixed Costs (Dynamic CAPEX/Maint)($) | 42500 | 42500 | 42500 | 42500 | 42500 | 8666.6667 | 8666.6667
Total annualized cost (Uravu + air cooled chiller ($/MW) | 355158.6131 | 352990.9507 | 352966.6667 | 352966.6667 | 352966.6667 | 352966.6667 | 352966.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 212912.25 | 145572 | 111966.75 | 103014 | 101759.75 | 67796.6667 | 67796.6667
Total avoided cost (Air-cooled chiller($/MW)) | 471833.3333 | 471833.3333 | 471833.3333 | 471833.3333 | 471833.3333 | 471833.3333 | 471833.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 319133.3333 | 319133.3333 | 319133.3333 | 319133.3333 | 319133.3333 | 319133.3333 | 319133.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | 106221.0833 | 173561.3333 | 207166.5833 | 216119.3333 | 217373.5833 | 251336.6667 | 251336.6667
Net cost allocated to water (Air-cooled chiller) | -116674.7202 | -118842.3826 | -118866.6667 | -118866.6667 | -118866.6667 | -118866.6667 | -118866.6667
LCOW (Gross Production) | 22.7328 | 22.7328 | 22.7328 | 22.7328 | 22.7328 | 22.7328 | 22.7328
LCOW (Net Delivered, No Credit) | 22.7917 | 22.7388 | 22.7328 | 22.7328 | 22.7328 | 22.7328 | 22.7328
Fair LCOW (Dry cooler + Air cooled chiller) | 10.1589 | 14.779 | 17.1671 | 17.8048 | 17.8942 | 20.3135 | 20.3135
Fair LCOW (Air cooled chiller) | -8.3326 | -8.4677 | -8.4672 | -8.4672 | -8.4672 | -8.4672 | -8.4672
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 1766612.9764 | 1752161.8935 | 1752000 | 1752000 | 1752000 | 1752000 | 1752000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 1136081.6667 | 687146.6667 | 463111.6667 | 403426.6667 | 395065 | 394200 | 394200
PUE_uravu | 1.2017 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.1297 | 1.0784 | 1.0529 | 1.0461 | 1.0451 | 1.045 | 1.045
WUE | -1.5984 | -1.6021 | -1.6026 | -1.6026 | -1.6026 | -1.6026 | -1.6026
Grid CO₂ (kg/kWh) | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013
Grid water (L/kWh) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Uravu water foot print (m3/year) | 883.3065 | 876.0809 | 876 | 876 | 876 | 876 | 876
Uravu CO2 emission (tCO₂/yr) | 22.966 | 22.7781 | 22.776 | 22.776 | 22.776 | 22.776 | 22.776

## Hyderabad
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-electric system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
CAPEX ($) | 650000 | 650000 | 650000 | 650000 | 650000 | 650000 | 650000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 100 | 100 | 100 | 100 | 100 | 100 | 100
Rated Power (Normal Operation) (kW) | 20 | 20 | 20 | 20 | 20 | 20 | 20
Uravu electrical consumption (kWh) | 175200 | 175200 | 175200 | 175200 | 175200 | 175200 | 175200
Waste heat Utulization (hr) | 5501 | 7799 | 8559 | 8760 | 8760 | 8760 | 8760
Waste heat downtime (hr) | 3259 | 961 | 201 | 0 | 0 | 0 | 0
Chiller required with waste heat (hr) | 3872 | 1615 | 0 | 0 | 0 | 0 | 0
Chiller requried without waste heat utulization (hr) | 2929 | 412 | 0 | 0 | 0 | 0 | 0
Fraction of time chiller is required (%) | 77.637 | 23.1393 | 0 | 0 | 0 | 0 | 0
Reduction in Chiller heat load (%) | 68.2753 | 96.5988 | 100 | 100 | 100 | 100 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 13369.9634 | 13369.9634 | 13369.9634 | 13369.9634 | 13369.9634 | 13369.9634 | 13369.9634
Water used for cooling in when waste heat is utlized (m³/MW/year) | 2848.5245 | 2213.9447 | 1135.2723 | 308.8264 | 9.7367 | 0 | 0
Water used for cooling when waste heat is not utilized (m³/MW/year) | 2841.3157 | 1303.5936 | 295.3469 | 0 | 0 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 7680.1232 | 9852.4251 | 11939.3442 | 13061.137 | 13360.2267 | 13369.9634 | 13369.9634
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 13 | 359 | 1824 | 5595 | 7829 | 8574 | 8760
Hours Air-cooled Chiller Required | 8747 | 8401 | 6936 | 3165 | 931 | 186 | 0
Electricity Cost ($) | 291625.1667 | 281648.8333 | 239408 | 130677.5 | 66263.8333 | 44783 | 39420
Fixed Costs (Dynamic CAPEX/Maint)($) | 42500 | 42500 | 42500 | 42500 | 42500 | 42500 | 8666.6667
Total annualized cost (Uravu + air cooled chiller ($/MW) | 364072.2748 | 275949.0113 | 265366.6667 | 265366.6667 | 265366.6667 | 265366.6667 | 265366.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 334125.1667 | 324148.8333 | 281908 | 173177.5 | 108763.8333 | 87283 | 48086.6667
Total avoided cost (Air-cooled chiller($/MW)) | 325833.3333 | 325833.3333 | 325833.3333 | 325833.3333 | 325833.3333 | 325833.3333 | 325833.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 231533.3333 | 231533.3333 | 231533.3333 | 231533.3333 | 231533.3333 | 231533.3333 | 231533.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | -102591.8333 | -92615.5 | -50374.6667 | 58355.8333 | 122769.5 | 144250.3333 | 183446.6667
Net cost allocated to water (Air-cooled chiller) | 38238.9414 | -49884.3221 | -60466.6667 | -60466.6667 | -60466.6667 | -60466.6667 | -60466.6667
LCOW (Gross Production) | 17.3174 | 17.3174 | 17.3174 | 17.3174 | 17.3174 | 17.3174 | 17.3174
LCOW (Net Delivered, No Credit) | 21.9908 | 19.1883 | 17.7086 | 17.3174 | 17.3174 | 17.3174 | 17.3174
Fair LCOW (Dry cooler + Air cooled chiller) | 2.8443 | -3.9946 | -1.2651 | 6.8952 | 11.713 | 13.3197 | 16.2514
Fair LCOW (Air cooled chiller) | 3.6319 | -4.1342 | -4.6247 | -4.5226 | -4.5226 | -4.5226 | -4.5226
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 2739056.081 | 1857823.446 | 1752000 | 1752000 | 1752000 | 1752000 | 1752000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 2916251.6667 | 2816488.3333 | 2394080 | 1306775 | 662638.3333 | 447830 | 394200
PUE_uravu | 1.3127 | 1.2121 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.3329 | 1.3215 | 1.2733 | 1.1492 | 1.0756 | 1.0511 | 1.045
WUE | -1.2019 | -1.3774 | -1.4925 | -1.5263 | -1.5263 | -1.5263 | -1.5263
Grid CO₂ (kg/kWh) | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73
Grid water (L/kWh) | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
Uravu water foot print (m3/year) | 6299.829 | 4272.9939 | 4029.6 | 4029.6 | 4029.6 | 4029.6 | 4029.6
Uravu CO2 emission (tCO₂/yr) | 1999.5109 | 1356.2111 | 1278.96 | 1278.96 | 1278.96 | 1278.96 | 1278.96

## Bengaluru
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-electric system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095
CAPEX ($) | 650000 | 650000 | 650000 | 650000 | 650000 | 650000 | 650000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 100 | 100 | 100 | 100 | 100 | 100 | 100
Rated Power (Normal Operation) (kW) | 20 | 20 | 20 | 20 | 20 | 20 | 20
Uravu electrical consumption (kWh) | 175200 | 175200 | 175200 | 175200 | 175200 | 175200 | 175200
Waste heat Utulization (hr) | 7467 | 8630 | 8759 | 8760 | 8760 | 8760 | 8760
Waste heat downtime (hr) | 1293 | 130 | 1 | 0 | 0 | 0 | 0
Chiller required with waste heat (hr) | 5269 | 217 | 2 | 0 | 0 | 0 | 0
Chiller requried without waste heat utulization (hr) | 1051 | 15 | 0 | 0 | 0 | 0 | 0
Fraction of time chiller is required (%) | 72.1461 | 2.6484 | 0.022831 | 0 | 0 | 0 | 0
Reduction in Chiller heat load (%) | 79.6698 | 99.558 | 99.9946 | 100 | 100 | 100 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 13369.9634 | 13369.9634 | 13369.9634 | 13369.9634 | 13369.9634 | 13369.9634 | 13369.9634
Water used for cooling in when waste heat is utlized (m³/MW/year) | 2963.6747 | 1631.2771 | 282.6218 | 3.8941 | 0 | 0 | 0
Water used for cooling when waste heat is not utilized (m³/MW/year) | 1373.2099 | 185.2612 | 1.4694 | 0 | 0 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 9033.0787 | 11553.4251 | 13085.8721 | 13366.0692 | 13369.9634 | 13369.9634 | 13369.9634
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 1 | 427 | 4232 | 7534 | 8641 | 8760 | 8760
Hours Air-cooled Chiller Required | 8759 | 8333 | 4528 | 1226 | 119 | 0 | 0
Electricity Cost ($) | 277372.6083 | 265703.7583 | 161478.4667 | 71031.1833 | 40708.6083 | 37449 | 37449
Fixed Costs (Dynamic CAPEX/Maint)($) | 42500 | 42500 | 42500 | 42500 | 42500 | 8666.6667 | 8666.6667
Total annualized cost (Uravu + air cooled chiller ($/MW) | 316697.6975 | 257913.2166 | 256622.5217 | 256606.6667 | 256606.6667 | 256606.6667 | 256606.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 319872.6083 | 308203.7583 | 203978.4667 | 113531.1833 | 83208.6083 | 46115.6667 | 46115.6667
Total avoided cost (Air-cooled chiller($/MW)) | 311233.3333 | 311233.3333 | 311233.3333 | 311233.3333 | 311233.3333 | 311233.3333 | 311233.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 222773.3333 | 222773.3333 | 222773.3333 | 222773.3333 | 222773.3333 | 222773.3333 | 222773.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | -97099.275 | -85430.425 | 18794.8667 | 109242.15 | 139564.725 | 176657.6667 | 176657.6667
Net cost allocated to water (Air-cooled chiller) | 5464.3642 | -53320.1168 | -54610.8116 | -54626.6667 | -54626.6667 | -54626.6667 | -54626.6667
LCOW (Gross Production) | 16.6622 | 16.6622 | 16.6622 | 16.6622 | 16.6622 | 16.6622 | 16.6622
LCOW (Net Delivered, No Credit) | 18.5695 | 16.8963 | 16.6641 | 16.6622 | 16.6622 | 16.6622 | 16.6622
Fair LCOW (Dry cooler + Air cooled chiller) | -0.26465 | -3.8143 | 3.9379 | 10.7013 | 12.9692 | 15.7436 | 15.7436
Fair LCOW (Air cooled chiller) | 0.45549 | -4.0441 | -4.085 | -4.0858 | -4.0858 | -4.0858 | -4.0858
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 2384537.1669 | 1765753.1568 | 1752166.895 | 1752000 | 1752000 | 1752000 | 1752000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 2919711.6667 | 2796881.6667 | 1699773.3333 | 747696.6667 | 428511.6667 | 394200 | 394200
PUE_uravu | 1.2722 | 1.2016 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.3333 | 1.3193 | 1.194 | 1.0854 | 1.0489 | 1.045 | 1.045
WUE | -1.3695 | -1.5051 | -1.5261 | -1.5263 | -1.5263 | -1.5263 | -1.5263
Grid CO₂ (kg/kWh) | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71
Grid water (L/kWh) | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
Uravu water foot print (m3/year) | 5484.4355 | 4061.2323 | 4029.9839 | 4029.6 | 4029.6 | 4029.6 | 4029.6
Uravu CO2 emission (tCO₂/yr) | 1693.0214 | 1253.6847 | 1244.0385 | 1243.92 | 1243.92 | 1243.92 | 1243.92

## Mumbai
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-electric system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.083 | 0.083 | 0.083 | 0.083 | 0.083 | 0.083 | 0.083
CAPEX ($) | 650000 | 650000 | 650000 | 650000 | 650000 | 650000 | 650000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 100 | 100 | 100 | 100 | 100 | 100 | 100
Rated Power (Normal Operation) (kW) | 20 | 20 | 20 | 20 | 20 | 20 | 20
Uravu electrical consumption (kWh) | 175200 | 175200 | 175200 | 175200 | 175200 | 175200 | 175200
Waste heat Utulization (hr) | 4646 | 8469 | 8760 | 8760 | 8760 | 8760 | 8760
Waste heat downtime (hr) | 4114 | 291 | 0 | 0 | 0 | 0 | 0
Chiller required with waste heat (hr) | 3888 | 5044 | 51 | 0 | 0 | 0 | 0
Chiller requried without waste heat utulization (hr) | 4105 | 247 | 0 | 0 | 0 | 0 | 0
Fraction of time chiller is required (%) | 91.2443 | 60.3995 | 0.58219 | 0 | 0 | 0 | 0
Reduction in Chiller heat load (%) | 48.3891 | 83.1365 | 99.8923 | 100 | 100 | 100 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 13369.9634 | 13369.9634 | 13369.9634 | 13369.9634 | 13369.9634 | 13369.9634 | 13369.9634
Water used for cooling in when waste heat is utlized (m³/MW/year) | 2984.5209 | 3089.2173 | 702.3956 | 11.8809 | 0 | 0 | 0
Water used for cooling when waste heat is not utilized (m³/MW/year) | 2130.9038 | 298.1818 | 0 | 0 | 0 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 8254.5387 | 9982.5642 | 12667.5678 | 13358.0825 | 13369.9634 | 13369.9634 | 13369.9634
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 0 | 92 | 1130 | 5183 | 8560 | 8760 | 8760
Hours Air-cooled Chiller Required | 8760 | 8668 | 7630 | 3577 | 200 | 0 | 0
Electricity Cost ($) | 242360 | 240158.2867 | 215317.2167 | 118322.1717 | 37504.9333 | 32718.6 | 32718.6
Fixed Costs (Dynamic CAPEX/Maint)($) | 33833.3333 | 42500 | 42500 | 42500 | 42500 | 8666.6667 | 8666.6667
Total annualized cost (Uravu + air cooled chiller ($/MW) | 368862.2617 | 279130.9163 | 235860.723 | 235582.6667 | 235582.6667 | 235582.6667 | 235582.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 276193.3333 | 282658.2867 | 257817.2167 | 160822.1717 | 80004.9333 | 41385.2667 | 41385.2667
Total avoided cost (Air-cooled chiller($/MW)) | 276193.3333 | 276193.3333 | 276193.3333 | 276193.3333 | 276193.3333 | 276193.3333 | 276193.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 201749.3333 | 201749.3333 | 201749.3333 | 201749.3333 | 201749.3333 | 201749.3333 | 201749.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | -74444 | -80908.9533 | -56067.8833 | 40927.1617 | 121744.4 | 160364.0667 | 160364.0667
Net cost allocated to water (Air-cooled chiller) | 92668.9284 | 2937.5829 | -40332.6103 | -40610.6667 | -40610.6667 | -40610.6667 | -40610.6667
LCOW (Gross Production) | 15.0897 | 15.0897 | 15.0897 | 15.0897 | 15.0897 | 15.0897 | 15.0897
LCOW (Net Delivered, No Credit) | 17.9507 | 15.434 | 15.0897 | 15.0897 | 15.0897 | 15.0897 | 15.0897
Fair LCOW (Dry cooler + Air cooled chiller) | 8.2453 | -0.26985 | -1.6422 | 5.5917 | 11.6364 | 14.5249 | 14.5249
Fair LCOW (Air cooled chiller) | 8.2453 | 0.22473 | -3.0167 | -3.0375 | -3.0375 | -3.0375 | -3.0375
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 3357778.2539 | 2276677.7059 | 1755350.0766 | 1752000 | 1752000 | 1752000 | 1752000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 2920000 | 2893473.3333 | 2594183.3333 | 1425568.3333 | 451866.6667 | 394200 | 394200
PUE_uravu | 1.3833 | 1.2599 | 1.2004 | 1.2 | 1.2 | 1.2 | 1.2
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.3333 | 1.3303 | 1.2961 | 1.1627 | 1.0516 | 1.045 | 1.045
WUE | -1.283 | -1.4922 | -1.5263 | -1.5263 | -1.5263 | -1.5263 | -1.5263
Grid CO₂ (kg/kWh) | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73
Grid water (L/kWh) | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
Uravu water foot print (m3/year) | 7722.89 | 5236.3587 | 4037.3052 | 4029.6 | 4029.6 | 4029.6 | 4029.6
Uravu CO2 emission (tCO₂/yr) | 2451.1781 | 1661.9747 | 1281.4056 | 1278.96 | 1278.96 | 1278.96 | 1278.96

## New Delhi
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-electric system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
CAPEX ($) | 650000 | 650000 | 650000 | 650000 | 650000 | 650000 | 650000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 100 | 100 | 100 | 100 | 100 | 100 | 100
Rated Power (Normal Operation) (kW) | 20 | 20 | 20 | 20 | 20 | 20 | 20
Uravu electrical consumption (kWh) | 175200 | 175200 | 175200 | 175200 | 175200 | 175200 | 175200
Waste heat Utulization (hr) | 5321 | 7452 | 8487 | 8759 | 8760 | 8760 | 8760
Waste heat downtime (hr) | 3439 | 1308 | 273 | 1 | 0 | 0 | 0
Chiller required with waste heat (hr) | 1607 | 2056 | 98 | 0 | 0 | 0 | 0
Chiller requried without waste heat utulization (hr) | 3170 | 735 | 0 | 0 | 0 | 0 | 0
Fraction of time chiller is required (%) | 54.532 | 31.8607 | 1.1187 | 0 | 0 | 0 | 0
Reduction in Chiller heat load (%) | 70.7569 | 90.1193 | 99.8651 | 100 | 100 | 100 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 13369.9634 | 13369.9634 | 13369.9634 | 13369.9634 | 13369.9634 | 13369.9634 | 13369.9634
Water used for cooling in when waste heat is utlized (m³/MW/year) | 1762.1931 | 1957.8639 | 1323.2209 | 392.4322 | 29.4867 | 0 | 0
Water used for cooling when waste heat is not utilized (m³/MW/year) | 2315.8499 | 1573.1528 | 401.1429 | 1.4694 | 0 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 9291.9204 | 9838.9467 | 11645.5996 | 12976.0618 | 13340.4767 | 13369.9634 | 13369.9634
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 1029 | 2151 | 3515 | 5377 | 7496 | 8502 | 8759
Hours Air-cooled Chiller Required | 7731 | 6609 | 5245 | 3383 | 1264 | 258 | 1
Electricity Cost ($) | 262330.5 | 229979.5 | 190650.8333 | 136963.1667 | 75865.3333 | 46859 | 39448.8333
Fixed Costs (Dynamic CAPEX/Maint)($) | 42500 | 42500 | 42500 | 42500 | 42500 | 42500 | 42500
Total annualized cost (Uravu + air cooled chiller ($/MW) | 356351.3499 | 296108.5433 | 265786.5212 | 265366.6667 | 265366.6667 | 265366.6667 | 265366.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 304830.5 | 272479.5 | 233150.8333 | 179463.1667 | 118365.3333 | 89359 | 81948.8333
Total avoided cost (Air-cooled chiller($/MW)) | 325833.3333 | 325833.3333 | 325833.3333 | 325833.3333 | 325833.3333 | 325833.3333 | 325833.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 231533.3333 | 231533.3333 | 231533.3333 | 231533.3333 | 231533.3333 | 231533.3333 | 231533.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | -73297.1667 | -40946.1667 | -1617.5 | 52070.1667 | 113168 | 142174.3333 | 149584.5
Net cost allocated to water (Air-cooled chiller) | 30518.0166 | -29724.79 | -60046.8121 | -60466.6667 | -60466.6667 | -60466.6667 | -60466.6667
LCOW (Gross Production) | 17.3174 | 17.3174 | 17.3174 | 17.3174 | 17.3174 | 17.3174 | 17.3174
LCOW (Net Delivered, No Credit) | 20.9454 | 19.6268 | 17.8531 | 17.3193 | 17.3174 | 17.3174 | 17.3174
Fair LCOW (Dry cooler + Air cooled chiller) | 4.6608 | 2.003 | 2.5165 | 6.4258 | 10.9949 | 13.1644 | 13.7186
Fair LCOW (Air cooled chiller) | 2.7608 | -2.5197 | -4.6301 | -4.5231 | -4.5226 | -4.5226 | -4.5226
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 2661846.8328 | 2059418.7663 | 1756198.5454 | 1752000 | 1752000 | 1752000 | 1752000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 2623305 | 2299795 | 1906508.3333 | 1369631.6667 | 758653.3333 | 468590 | 394488.3333
PUE_uravu | 1.3039 | 1.2351 | 1.2005 | 1.2 | 1.2 | 1.2 | 1.2
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.2995 | 1.2625 | 1.2176 | 1.1564 | 1.0866 | 1.0535 | 1.045
WUE | -1.2619 | -1.3467 | -1.4805 | -1.5261 | -1.5263 | -1.5263 | -1.5263
Grid CO₂ (kg/kWh) | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73
Grid water (L/kWh) | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
Uravu water foot print (m3/year) | 6122.2477 | 4736.6632 | 4039.2567 | 4029.6 | 4029.6 | 4029.6 | 4029.6
Uravu CO2 emission (tCO₂/yr) | 1943.1482 | 1503.3757 | 1282.0249 | 1278.96 | 1278.96 | 1278.96 | 1278.96

## Chennai
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-electric system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09
CAPEX ($) | 650000 | 650000 | 650000 | 650000 | 650000 | 650000 | 650000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 100 | 100 | 100 | 100 | 100 | 100 | 100
Rated Power (Normal Operation) (kW) | 20 | 20 | 20 | 20 | 20 | 20 | 20
Uravu electrical consumption (kWh) | 175200 | 175200 | 175200 | 175200 | 175200 | 175200 | 175200
Waste heat Utulization (hr) | 3961 | 7780 | 8696 | 8760 | 8760 | 8760 | 8760
Waste heat downtime (hr) | 4799 | 980 | 64 | 0 | 0 | 0 | 0
Chiller required with waste heat (hr) | 3939 | 5386 | 107 | 1 | 0 | 0 | 0
Chiller requried without waste heat utulization (hr) | 4799 | 937 | 7 | 0 | 0 | 0 | 0
Fraction of time chiller is required (%) | 99.7489 | 72.1804 | 1.3014 | 0.011416 | 0 | 0 | 0
Reduction in Chiller heat load (%) | 41.1045 | 81.8027 | 99.8085 | 99.999 | 100 | 100 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 13369.9634 | 13369.9634 | 13369.9634 | 13369.9634 | 13369.9634 | 13369.9634 | 13369.9634
Water used for cooling in when waste heat is utlized (m³/MW/year) | 2916.6852 | 2601.6173 | 1354.4844 | 143.9095 | 1.2057 | 0 | 0
Water used for cooling when waste heat is not utilized (m³/MW/year) | 2383.2783 | 1037.1001 | 91.8172 | 0 | 0 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 8069.9999 | 9731.246 | 11923.6617 | 13226.0539 | 13368.7577 | 13369.9634 | 13369.9634
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 0 | 1 | 620 | 4184 | 7862 | 8704 | 8760
Hours Air-cooled Chiller Required | 8760 | 8759 | 8140 | 4576 | 898 | 56 | 0
Electricity Cost ($) | 262800 | 262774.05 | 246711 | 154225.2 | 58781.1 | 36931.2 | 35478
Fixed Costs (Dynamic CAPEX/Maint)($) | 33833.3333 | 42500 | 42500 | 42500 | 42500 | 42500 | 8666.6667
Total annualized cost (Uravu + air cooled chiller ($/MW) | 412764.9748 | 298802.4831 | 248382.8426 | 247849.5562 | 247846.6667 | 247846.6667 | 247846.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 296633.3333 | 305274.05 | 289211 | 196725.2 | 101281.1 | 79431.2 | 44144.6667
Total avoided cost (Air-cooled chiller($/MW)) | 296633.3333 | 296633.3333 | 296633.3333 | 296633.3333 | 296633.3333 | 296633.3333 | 296633.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 214013.3333 | 214013.3333 | 214013.3333 | 214013.3333 | 214013.3333 | 214013.3333 | 214013.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | -82620 | -91260.7167 | -75197.6667 | 17288.1333 | 112732.2333 | 134582.1333 | 169868.6667
Net cost allocated to water (Air-cooled chiller) | 116131.6414 | 2169.1498 | -48250.4907 | -48783.7771 | -48786.6667 | -48786.6667 | -48786.6667
LCOW (Gross Production) | 16.007 | 16.007 | 16.007 | 16.007 | 16.007 | 16.007 | 16.007
LCOW (Net Delivered, No Credit) | 19.4793 | 17.3531 | 16.1177 | 16.007 | 16.007 | 16.007 | 16.007
Fair LCOW (Dry cooler + Air cooled chiller) | 10.5702 | -0.52474 | -3.0748 | 3.8238 | 10.9623 | 12.5966 | 15.2358
Fair LCOW (Air cooled chiller) | 10.5702 | 0.17588 | -3.6338 | -3.6488 | -3.649 | -3.649 | -3.649
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 3584425.6454 | 2318175.7382 | 1757957.5107 | 1752032.1064 | 1752000 | 1752000 | 1752000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 2920000 | 2919711.6667 | 2741233.3333 | 1713613.3333 | 653123.3333 | 410346.6667 | 394200
PUE_uravu | 1.4092 | 1.2646 | 1.2007 | 1.2 | 1.2 | 1.2 | 1.2
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.3333 | 1.3333 | 1.3129 | 1.1956 | 1.0746 | 1.0468 | 1.045
WUE | -1.2542 | -1.4079 | -1.5158 | -1.5263 | -1.5263 | -1.5263 | -1.5263
Grid CO₂ (kg/kWh) | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
Grid water (L/kWh) | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
Uravu water foot print (m3/year) | 8244.179 | 5331.8042 | 4043.3023 | 4029.6738 | 4029.6 | 4029.6 | 4029.6
Uravu CO2 emission (tCO₂/yr) | 2688.3192 | 1738.6318 | 1318.4681 | 1314.0241 | 1314 | 1314 | 1314

## Singapore
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-electric system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
CAPEX ($) | 650000 | 650000 | 650000 | 650000 | 650000 | 650000 | 650000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 100 | 100 | 100 | 100 | 100 | 100 | 100
Rated Power (Normal Operation) (kW) | 20 | 20 | 20 | 20 | 20 | 20 | 20
Uravu electrical consumption (kWh) | 175200 | 175200 | 175200 | 175200 | 175200 | 175200 | 175200
Waste heat Utulization (hr) | 5300 | 8648 | 8760 | 8760 | 8760 | 8760 | 8760
Waste heat downtime (hr) | 3460 | 112 | 0 | 0 | 0 | 0 | 0
Chiller required with waste heat (hr) | 5300 | 7983 | 248 | 0 | 0 | 0 | 0
Chiller requried without waste heat utulization (hr) | 3460 | 112 | 0 | 0 | 0 | 0 | 0
Fraction of time chiller is required (%) | 100 | 92.4087 | 2.8311 | 0 | 0 | 0 | 0
Reduction in Chiller heat load (%) | 32.5424 | 74.8961 | 99.5179 | 100 | 100 | 100 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 13369.9634 | 13369.9634 | 13369.9634 | 13369.9634 | 13369.9634 | 13369.9634 | 13369.9634
Water used for cooling in when waste heat is utlized (m³/MW/year) | 4884.0922 | 3168.8264 | 483.8402 | 0.24759 | 0 | 0 | 0
Water used for cooling when waste heat is not utilized (m³/MW/year) | 1285.1445 | 75.5655 | 0 | 0 | 0 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 7200.7266 | 10125.5714 | 12886.1231 | 13369.7158 | 13369.9634 | 13369.9634 | 13369.9634
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 0 | 0 | 92 | 5921 | 8740 | 8760 | 8760
Hours Air-cooled Chiller Required | 8760 | 8760 | 8668 | 2839 | 20 | 0 | 0
Electricity Cost ($) | 584000 | 584000 | 578694.6667 | 242555.6667 | 79993.3333 | 78840 | 78840
Fixed Costs (Dynamic CAPEX/Maint)($) | 33833.3333 | 33833.3333 | 42500 | 42500 | 42500 | 8666.6667 | 8666.6667
Total annualized cost (Uravu + air cooled chiller ($/MW) | 860330.6772 | 596779.1086 | 443566.5757 | 440566.6667 | 440566.6667 | 440566.6667 | 440566.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 617833.3333 | 617833.3333 | 621194.6667 | 285055.6667 | 122493.3333 | 87506.6667 | 87506.6667
Total avoided cost (Air-cooled chiller($/MW)) | 617833.3333 | 617833.3333 | 617833.3333 | 617833.3333 | 617833.3333 | 617833.3333 | 617833.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 406733.3333 | 406733.3333 | 406733.3333 | 406733.3333 | 406733.3333 | 406733.3333 | 406733.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | -211100 | -211100 | -214461.3333 | 121677.6667 | 284240 | 319226.6667 | 319226.6667
Net cost allocated to water (Air-cooled chiller) | 242497.3439 | -21054.2247 | -174266.7576 | -177266.6667 | -177266.6667 | -177266.6667 | -177266.6667
LCOW (Gross Production) | 30.4214 | 30.4214 | 30.4214 | 30.4214 | 30.4214 | 30.4214 | 30.4214
LCOW (Net Delivered, No Credit) | 33.6566 | 30.5943 | 30.4214 | 30.4214 | 30.4214 | 30.4214 | 30.4214
Fair LCOW (Dry cooler + Air cooled chiller) | 20.0663 | -1.5837 | -13.2856 | 11.6314 | 23.7901 | 26.407 | 26.407
Fair LCOW (Air cooled chiller) | 20.0663 | -1.5837 | -13.0342 | -13.2586 | -13.2586 | -13.2586 | -13.2586
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 3850820.0528 | 2533062.2097 | 1766999.5454 | 1752000 | 1752000 | 1752000 | 1752000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 2920000 | 2920000 | 2893473.3333 | 1212778.3333 | 399966.6667 | 394200 | 394200
PUE_uravu | 1.4396 | 1.2892 | 1.2017 | 1.2 | 1.2 | 1.2 | 1.2
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.3333 | 1.3333 | 1.3303 | 1.1384 | 1.0457 | 1.045 | 1.045
WUE | -1.3795 | -1.5176 | -1.5263 | -1.5263 | -1.5263 | -1.5263 | -1.5263
Grid CO₂ (kg/kWh) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Grid water (L/kWh) | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
Uravu water foot print (m3/year) | 3080.656 | 2026.4498 | 1413.5996 | 1401.6 | 1401.6 | 1401.6 | 1401.6
Uravu CO2 emission (tCO₂/yr) | 1540.328 | 1013.2249 | 706.7998 | 700.8 | 700.8 | 700.8 | 700.8