## Phoenix
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-waste heat system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13
CAPEX ($) | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286
Rated Power (Normal Operation) (kW) | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958
Rated Power (with Pre-Cooling) (kW) | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458
Uravu electrical consumption (kWh) | 13662.0717 | 26727.2318 | 36681.155 | 43331.8244 | 43761.0555 | 43974.1635 | 44198.5034
System Downtime Trigger (WBT) (deg C) | 9.5 | 14.5 | 19.5 | 24.5 | 29.5 | 34.5 | 39.5
Vapor Temperature (deg C) | 12.5 | 17.5 | 22.5 | 27.5 | 32.5 | 37.5 | 42.5
Facility water outlet temperature (deg C) | 23.5 | 28.5 | 33.5 | 38.5 | 43.5 | 48.5 | 53.5
Hours evaporative cooler is operational for facility water | 330 | 1263 | 1817 | 1690 | 661 | 96 | 0
Hours chiller is operational for facility water cooling | 119 | 866 | 1349 | 1147 | 340 | 23 | 0
Total downtime due to WBT trigger | 5964 | 3430 | 1470 | 3 | 0 | 0 | 0
Total downtine due to high water usage | 141 | 136 | 144 | 184 | 100 | 55 | 10
Annual Downtime Hours (hr) | 6105 | 3566 | 1614 | 187 | 100 | 55 | 10
Reduction in chiller load (%) | 28.9498 | 49.4064 | 66.1758 | 84.7717 | 94.9772 | 99.1096 | 99.8858
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 3413.5714 | 6678 | 9187.7143 | 11022.4286 | 11134.2857 | 11192.1429 | 11250
water used for pre-cooling in Uravu (m³/MW/year) | 1835.7686 | 3394.1571 | 4524.7886 | 4608.8743 | 3031.4314 | 2119.3714 | 1023.0429
Water used for cooling faciltiy water (m³/MW/year) | 64.8367 | 295.9347 | 436.5551 | 391.2 | 145.8735 | 16.8367 | 0
Net Water Delivered to Customer (m³/MW/year) | 1512.9661 | 2987.9082 | 4226.3706 | 6022.3543 | 7956.9808 | 9055.9347 | 10226.9571
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 1742 | 3170 | 4483 | 5918 | 7351 | 8285 | 8709
Hours Air-cooled Chiller Required | 7018 | 5590 | 4277 | 2842 | 1409 | 475 | 51
Electricity Cost ($) | 314304.0333 | 260777.8333 | 211562.2167 | 157773.6333 | 104060.0167 | 69050.5833 | 53157.65
Total annualized cost (Uravu + Air cooled chiller ($/MW) | 359993.0417 | 276026.9444 | 210915.5417 | 156147.9861 | 141446.25 | 136293.375 | 134475
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 356804.0333 | 303277.8333 | 254062.2167 | 200273.6333 | 146560.0167 | 111550.5833 | 95657.65
Total avoided cost (Air-cooled chiller($/MW)) | 413433.3333 | 413433.3333 | 413433.3333 | 413433.3333 | 413433.3333 | 413433.3333 | 413433.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 60590.8333 | 77094.3333 | 89782.3333 | 99057.8333 | 99623.3333 | 99915.8333 | 100208.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | 3189.0083 | -27250.8889 | -43146.675 | -44125.6472 | -5113.7667 | 24742.7917 | 38817.35
Net cost allocated to water (Air-cooled chiller) | -53440.2917 | -137406.3889 | -202517.7917 | -257285.3472 | -271987.0833 | -277139.9583 | -278958.3333
NVW (Gross Production) | 17.75 | 11.5445 | 9.772 | 8.9869 | 8.9474 | 8.9273 | 8.9074
NVW (Net Delivered, No Credit) | 40.0477 | 25.8021 | 21.2434 | 16.4484 | 12.5202 | 11.0332 | 9.7985
Fair NVW (Dry cooler + Air cooled chiller) | 2.1078 | -9.1204 | -10.2089 | -7.327 | -0.64268 | 2.7322 | 3.7956
Fair NVW (Air cooled chiller) | -35.3215 | -45.9875 | -47.9177 | -42.7217 | -34.1822 | -30.6031 | -27.2768
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 2175587.5 | 1529694.4444 | 1028837.5 | 607548.6111 | 494458.3333 | 454820.8333 | 440833.3333
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 2417723.3333 | 2005983.3333 | 1627401.6667 | 1213643.3333 | 800461.6667 | 531158.3333 | 408905
PUE_uravu | 1.2484 | 1.1746 | 1.1174 | 1.0694 | 1.0564 | 1.0519 | 1.0503
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.276 | 1.229 | 1.1858 | 1.1385 | 1.0914 | 1.0606 | 1.0467
WUE | -0.17271 | -0.34109 | -0.48246 | -0.68748 | -0.90833 | -1.0338 | -1.1675
Grid CO₂ (kg/kWh) | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
Grid water (L/kWh) | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Uravu water foot print (m3/year) | 5438.9688 | 3824.2361 | 2572.0938 | 1518.8715 | 1236.1458 | 1137.0521 | 1102.0833
Uravu CO2 emission (tCO₂/yr) | 979.0144 | 688.3625 | 462.9769 | 273.3969 | 222.5063 | 204.6694 | 198.375
Cooling tower + Air cooled chiller mixed mode analysis
Variable | Value | Value | Value | Value | Value | Value | Value
Hours Cooling is Sufficient | 5069 | 7105 | 8753 | 8760 | 8760 | 8760 | 8760
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 245046.0172 | 172192.0328 | 113221.8136 | 112971.3333 | 112971.3333 | 112971.3333 | 112971.3333
Fair NVW (Dry cooler + Air cooled chiller) | 75.9746 | 34.7517 | 23.1153 | 7.1694 | 3.5786 | 2.5753 | 2.1026
Stand-alonecooling tower + air-cooled chiller power consumption | 1281023.3333 | 622716.6667 | 89863.3333 | 87600 | 87600 | 87600 | 87600
PUE_Cooling_tower_chiller | 1.1462 | 1.0711 | 1.0103 | 1.01 | 1.01 | 1.01 | 1.01

## Chicago
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-waste heat system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
CAPEX ($) | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286
Rated Power (Normal Operation) (kW) | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958
Rated Power (with Pre-Cooling) (kW) | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458
Uravu electrical consumption (kWh) | 24401.3348 | 30285.7114 | 38127.4147 | 42703.8076 | 43194.6235 | 43198.967 | 43198.967
System Downtime Trigger (WBT) (deg C) | 9.5 | 14.5 | 19.5 | 24.5 | 29.5 | 34.5 | 39.5
Vapor Temperature (deg C) | 12.5 | 17.5 | 22.5 | 27.5 | 32.5 | 37.5 | 42.5
Facility water outlet temperature (deg C) | 23.5 | 28.5 | 33.5 | 38.5 | 43.5 | 48.5 | 53.5
Hours evaporative cooler is operational for facility water | 2 | 1 | 24 | 23 | 0 | 0 | 0
Hours chiller is operational for facility water cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total downtime due to WBT trigger | 4012 | 2851 | 1101 | 85 | 0 | 0 | 0
Total downtine due to high water usage | 6 | 23 | 62 | 29 | 1 | 0 | 0
Annual Downtime Hours (hr) | 4018 | 2874 | 1163 | 114 | 1 | 0 | 0
Reduction in chiller load (%) | 54.1324 | 67.1918 | 86.7237 | 98.6986 | 99.9886 | 100 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 6096.8571 | 7567.7143 | 9767.5714 | 11116.2857 | 11261.5714 | 11262.8571 | 11262.8571
water used for pre-cooling in Uravu (m³/MW/year) | 884.1086 | 1116.4371 | 1295.3314 | 1258.0714 | 1508.76 | 374.4 | 0
Water used for cooling faciltiy water (m³/MW/year) | 0.097959 | 0.17143 | 3.1224 | 3.2449 | 0 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 5212.6506 | 6451.1057 | 8469.1176 | 9854.9694 | 9752.8114 | 10888.4571 | 11262.8571
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 5011 | 6060 | 7505 | 8502 | 8742 | 8760 | 8760
Hours Air-cooled Chiller Required | 3749 | 2700 | 1255 | 258 | 18 | 0 | 0
Electricity Cost ($) | 177019.4 | 140724 | 90727 | 56230.8 | 47926.8 | 47304 | 47304
Total annualized cost (Uravu + Air cooled chiller ($/MW) | 266338.6667 | 227442.6667 | 169268.6667 | 133602.6667 | 129760.6667 | 129726.6667 | 129726.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 219519.4 | 183224 | 133227 | 98730.8 | 90426.8 | 55970.6667 | 55970.6667
Total avoided cost (Air-cooled chiller($/MW)) | 384233.3333 | 384233.3333 | 384233.3333 | 384233.3333 | 384233.3333 | 384233.3333 | 384233.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 71785.3333 | 78649.3333 | 88915.3333 | 95209.3333 | 95887.3333 | 95893.3333 | 95893.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | 46819.2667 | 44218.6667 | 36041.6667 | 34871.8667 | 39333.8667 | 73756 | 73756
Net cost allocated to water (Air-cooled chiller) | -117894.6667 | -156790.6667 | -214964.6667 | -250630.6667 | -254472.6667 | -254506.6667 | -254506.6667
NVW (Gross Production) | 11.7742 | 10.3927 | 9.1031 | 8.5649 | 8.5146 | 8.5141 | 8.5141
NVW (Net Delivered, No Credit) | 13.7714 | 12.1916 | 10.4988 | 9.661 | 9.8318 | 8.8069 | 8.5141
Fair NVW (Dry cooler + Air cooled chiller) | 8.9819 | 6.8544 | 4.2557 | 3.5385 | 4.0331 | 6.7738 | 6.5486
Fair NVW (Air cooled chiller) | -22.617 | -24.3045 | -25.3822 | -25.4319 | -26.0922 | -23.374 | -22.597
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 1576433.3333 | 1252300 | 767516.6667 | 470300 | 438283.3333 | 438000 | 438000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 1475161.6667 | 1172700 | 756058.3333 | 468590 | 399390 | 394200 | 394200
PUE_uravu | 1.18 | 1.143 | 1.0876 | 1.0537 | 1.05 | 1.05 | 1.05
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.1684 | 1.1339 | 1.0863 | 1.0535 | 1.0456 | 1.045 | 1.045
WUE | -0.59505 | -0.73643 | -0.96679 | -1.125 | -1.1133 | -1.243 | -1.2857
Grid CO₂ (kg/kWh) | 0.334 | 0.334 | 0.334 | 0.334 | 0.334 | 0.334 | 0.334
Grid water (L/kWh) | 3.97 | 3.97 | 3.97 | 3.97 | 3.97 | 3.97 | 3.97
Uravu water foot print (m3/year) | 6258.4403 | 4971.631 | 3047.0412 | 1867.091 | 1739.9848 | 1738.86 | 1738.86
Uravu CO2 emission (tCO₂/yr) | 526.5287 | 418.2682 | 256.3506 | 157.0802 | 146.3866 | 146.292 | 146.292
Cooling tower + Air cooled chiller mixed mode analysis
Variable | Value | Value | Value | Value | Value | Value | Value
Hours Cooling is Sufficient | 5764 | 7470 | 8622 | 8760 | 8760 | 8760 | 8760
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 294174.4357 | 211818.3093 | 156206.2005 | 149544.3333 | 149544.3333 | 149544.3333 | 149544.3333
Fair NVW (Dry cooler + Air cooled chiller) | -5.34 | 2.422 | 1.5424 | -1.6176 | -2.0285 | -1.8201 | -1.7596
Stand-alonecooling tower + air-cooled chiller power consumption | 1056306.6667 | 504700 | 132220 | 87600 | 87600 | 87600 | 87600
PUE_Cooling_tower_chiller | 1.1206 | 1.0576 | 1.0151 | 1.01 | 1.01 | 1.01 | 1.01

## Houston
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-waste heat system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11
CAPEX ($) | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286
Rated Power (Normal Operation) (kW) | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958
Rated Power (with Pre-Cooling) (kW) | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458
Uravu electrical consumption (kWh) | 7065.1693 | 12560.8727 | 20717.298 | 34313.1562 | 39918.8214 | 40564.8691 | 40577.8996
System Downtime Trigger (WBT) (deg C) | 9.5 | 14.5 | 19.5 | 24.5 | 29.5 | 34.5 | 39.5
Vapor Temperature (deg C) | 12.5 | 17.5 | 22.5 | 27.5 | 32.5 | 37.5 | 42.5
Facility water outlet temperature (deg C) | 23.5 | 28.5 | 33.5 | 38.5 | 43.5 | 48.5 | 53.5
Hours evaporative cooler is operational for facility water | 47 | 88 | 131 | 343 | 92 | 1 | 0
Hours chiller is operational for facility water cooling | 5 | 10 | 28 | 103 | 6 | 0 | 0
Total downtime due to WBT trigger | 7322 | 6232 | 4431 | 1274 | 12 | 0 | 0
Total downtine due to high water usage | 65 | 87 | 128 | 165 | 139 | 3 | 0
Annual Downtime Hours (hr) | 7387 | 6319 | 4559 | 1439 | 151 | 3 | 0
Reduction in chiller load (%) | 15.6164 | 27.7511 | 47.637 | 82.3973 | 98.2078 | 99.9658 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 1765.2857 | 3138.4286 | 5401.2857 | 9412.7143 | 11068.7143 | 11259 | 11262.8571
water used for pre-cooling in Uravu (m³/MW/year) | 490.2429 | 732.0857 | 1205.0229 | 2104.0714 | 1350.8229 | 499.6286 | 13.1143
Water used for cooling faciltiy water (m³/MW/year) | 6.502 | 12.2204 | 22.9469 | 64.0653 | 7.9469 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 1268.5408 | 2394.1224 | 4173.3159 | 7244.5776 | 9709.9445 | 10759.3714 | 11249.7429
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 1456 | 2743 | 4692 | 7117 | 8344 | 8751 | 8760
Hours Air-cooled Chiller Required | 7304 | 6017 | 4068 | 1643 | 416 | 9 | 0
Electricity Cost ($) | 275020.5333 | 234201.1833 | 172385.4 | 95472.4833 | 56556.1333 | 43647.45 | 43362
Total annualized cost (Uravu + Air cooled chiller ($/MW) | 355619.9028 | 322389.6667 | 267679.6389 | 171160.5972 | 130109.9722 | 125440.1667 | 125346.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 317520.5333 | 276701.1833 | 214885.4 | 137972.4833 | 99056.1333 | 86147.45 | 52028.6667
Total avoided cost (Air-cooled chiller($/MW)) | 355033.3333 | 355033.3333 | 355033.3333 | 355033.3333 | 355033.3333 | 355033.3333 | 355033.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 50884.8333 | 56758.8333 | 66438.8333 | 83598.8333 | 90682.8333 | 91496.8333 | 91513.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | 38099.3694 | 45688.4833 | 52794.2389 | 33188.1139 | 31053.8389 | 39292.7167 | 73318
Net cost allocated to water (Air-cooled chiller) | 586.5694 | -32643.6667 | -87353.6944 | -183872.7361 | -224923.3611 | -229593.1667 | -229686.6667
NVW (Gross Production) | 28.8253 | 18.0851 | 12.3006 | 8.8815 | 8.1927 | 8.1266 | 8.1252
NVW (Net Delivered, No Credit) | 40.1129 | 23.7076 | 15.9199 | 11.5395 | 9.3392 | 8.5039 | 8.1347
Fair NVW (Dry cooler + Air cooled chiller) | 30.034 | 19.0836 | 12.6504 | 4.5811 | 3.1981 | 3.652 | 6.5173
Fair NVW (Air cooled chiller) | 0.4624 | -13.6349 | -20.9315 | -25.3807 | -23.1642 | -21.3389 | -20.4171
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 2531393.0556 | 2229300 | 1731936.1111 | 854490.2778 | 481302.7778 | 438850 | 438000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 2500186.6667 | 2129101.6667 | 1567140 | 867931.6667 | 514146.6667 | 396795 | 394200
PUE_uravu | 1.289 | 1.2545 | 1.1977 | 1.0975 | 1.0549 | 1.0501 | 1.05
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.2854 | 1.243 | 1.1789 | 1.0991 | 1.0587 | 1.0453 | 1.045
WUE | -0.14481 | -0.2733 | -0.47641 | -0.82701 | -1.1084 | -1.2282 | -1.2842
Grid CO₂ (kg/kWh) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Grid water (L/kWh) | 3 | 3 | 3 | 3 | 3 | 3 | 3
Uravu water foot print (m3/year) | 7594.1792 | 6687.9 | 5195.8083 | 2563.4708 | 1443.9083 | 1316.55 | 1314
Uravu CO2 emission (tCO₂/yr) | 1265.6965 | 1114.65 | 865.9681 | 427.2451 | 240.6514 | 219.425 | 219
Cooling tower + Air cooled chiller mixed mode analysis
Variable | Value | Value | Value | Value | Value | Value | Value
Hours Cooling is Sufficient | 2411 | 4130 | 7106 | 8731 | 8760 | 8760 | 8760
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 300362.272 | 252116.3023 | 168590.9935 | 122983.256 | 122169.3333 | 122169.3333 | 122169.3333
Fair NVW (Dry cooler + Air cooled chiller) | 43.56 | 29.3525 | 23.7434 | 6.6501 | 0.81778 | 0.304 | 0.28244
Stand-alonecooling tower + air-cooled chiller power consumption | 2140443.3333 | 1584633.3333 | 622393.3333 | 96976.6667 | 87600 | 87600 | 87600
PUE_Cooling_tower_chiller | 1.2443 | 1.1809 | 1.071 | 1.0111 | 1.01 | 1.01 | 1.01

## Seattle
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-waste heat system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
CAPEX ($) | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286
Rated Power (Normal Operation) (kW) | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958
Rated Power (with Pre-Cooling) (kW) | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458
Uravu electrical consumption (kWh) | 22950.2221 | 40003.3692 | 44514.572 | 44751.6662 | 44769.8425 | 44769.8425 | 44769.8425
System Downtime Trigger (WBT) (deg C) | 9.5 | 14.5 | 19.5 | 24.5 | 29.5 | 34.5 | 39.5
Vapor Temperature (deg C) | 12.5 | 17.5 | 22.5 | 27.5 | 32.5 | 37.5 | 42.5
Facility water outlet temperature (deg C) | 23.5 | 28.5 | 33.5 | 38.5 | 43.5 | 48.5 | 53.5
Hours evaporative cooler is operational for facility water | 0 | 6 | 17 | 0 | 0 | 0 | 0
Hours chiller is operational for facility water cooling | 0 | 0 | 2 | 0 | 0 | 0 | 0
Total downtime due to WBT trigger | 4291 | 937 | 31 | 0 | 0 | 0 | 0
Total downtine due to high water usage | 9 | 49 | 25 | 4 | 0 | 0 | 0
Annual Downtime Hours (hr) | 4300 | 986 | 56 | 4 | 0 | 0 | 0
Reduction in chiller load (%) | 50.9132 | 88.7443 | 99.3379 | 99.9543 | 100 | 100 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 5734.2857 | 9995.1429 | 11190.8571 | 11257.7143 | 11262.8571 | 11262.8571 | 11262.8571
water used for pre-cooling in Uravu (m³/MW/year) | 969.5057 | 1509.48 | 1710.3343 | 3434.9914 | 1239.7886 | 0 | 0
Water used for cooling faciltiy water (m³/MW/year) | 0 | 0.31837 | 2.3388 | 0 | 0 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 4764.78 | 8485.3445 | 9478.1841 | 7822.7229 | 10023.0686 | 11262.8571 | 11262.8571
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 5289 | 7818 | 8564 | 8745 | 8760 | 8760 | 8760
Hours Air-cooled Chiller Required | 3471 | 942 | 196 | 15 | 0 | 0 | 0
Electricity Cost ($) | 139500.5 | 66581 | 45071.3333 | 39852.5 | 39420 | 39420 | 39420
Total annualized cost (Uravu + Air cooled chiller ($/MW) | 242800 | 148903.3333 | 122561.3889 | 121080 | 120966.6667 | 120966.6667 | 120966.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 182000.5 | 109081 | 87571.3333 | 82352.5 | 48086.6667 | 48086.6667 | 48086.6667
Total avoided cost (Air-cooled chiller($/MW)) | 325833.3333 | 325833.3333 | 325833.3333 | 325833.3333 | 325833.3333 | 325833.3333 | 325833.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 65633.3333 | 82203.3333 | 86853.3333 | 87113.3333 | 87133.3333 | 87133.3333 | 87133.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | 60799.5 | 39822.3333 | 34990.0556 | 38727.5 | 72880 | 72880 | 72880
Net cost allocated to water (Air-cooled chiller) | -83033.3333 | -176930 | -203271.9444 | -204753.3333 | -204866.6667 | -204866.6667 | -204866.6667
NVW (Gross Production) | 11.4458 | 8.2243 | 7.7611 | 7.7381 | 7.7363 | 7.7363 | 7.7363
NVW (Net Delivered, No Credit) | 13.7747 | 9.6877 | 9.1635 | 11.1359 | 8.6933 | 7.7363 | 7.7363
Fair NVW (Dry cooler + Air cooled chiller) | 12.7602 | 4.6931 | 3.6916 | 4.9506 | 7.2712 | 6.4708 | 6.4708
Fair NVW (Air cooled chiller) | -17.4265 | -20.8512 | -21.4463 | -26.1742 | -20.4395 | -18.1896 | -18.1896
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 1656333.3333 | 717366.6667 | 453947.2222 | 439133.3333 | 438000 | 438000 | 438000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 1395005 | 665810 | 450713.3333 | 398525 | 394200 | 394200 | 394200
PUE_uravu | 1.1891 | 1.0819 | 1.0518 | 1.0501 | 1.05 | 1.05 | 1.05
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.1592 | 1.076 | 1.0515 | 1.0455 | 1.045 | 1.045 | 1.045
WUE | -0.54392 | -0.96865 | -1.082 | -0.893 | -1.1442 | -1.2857 | -1.2857
Grid CO₂ (kg/kWh) | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
Grid water (L/kWh) | 1 | 1 | 1 | 1 | 1 | 1 | 1
Uravu water foot print (m3/year) | 1656.3333 | 717.3667 | 453.9472 | 439.1333 | 438 | 438 | 438
Uravu CO2 emission (tCO₂/yr) | 33.1267 | 14.3473 | 9.0789 | 8.7827 | 8.76 | 8.76 | 8.76
Cooling tower + Air cooled chiller mixed mode analysis
Variable | Value | Value | Value | Value | Value | Value | Value
Hours Cooling is Sufficient | 7532 | 8705 | 8760 | 8760 | 8760 | 8760 | 8760
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 114128.2573 | 79134.1483 | 77493.3333 | 77493.3333 | 77493.3333 | 77493.3333 | 77493.3333
Fair NVW (Dry cooler + Air cooled chiller) | 27.0048 | 8.2223 | 4.7549 | 5.5718 | 4.3373 | 3.8599 | 3.8599
Stand-alonecooling tower + air-cooled chiller power consumption | 484653.3333 | 105383.3333 | 87600 | 87600 | 87600 | 87600 | 87600
PUE_Cooling_tower_chiller | 1.0553 | 1.012 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01

## Frankfurt
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-waste heat system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
CAPEX ($) | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286
Rated Power (Normal Operation) (kW) | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958
Rated Power (with Pre-Cooling) (kW) | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458
Uravu electrical consumption (kWh) | 25481.9507 | 37701.5967 | 43752.0309 | 44399.6274 | 44483.4265 | 44483.4265 | 44483.4265
System Downtime Trigger (WBT) (deg C) | 9.5 | 14.5 | 19.5 | 24.5 | 29.5 | 34.5 | 39.5
Vapor Temperature (deg C) | 12.5 | 17.5 | 22.5 | 27.5 | 32.5 | 37.5 | 42.5
Facility water outlet temperature (deg C) | 23.5 | 28.5 | 33.5 | 38.5 | 43.5 | 48.5 | 53.5
Hours evaporative cooler is operational for facility water | 6 | 54 | 52 | 4 | 0 | 0 | 0
Hours chiller is operational for facility water cooling | 1 | 12 | 11 | 0 | 0 | 0 | 0
Total downtime due to WBT trigger | 3788 | 1344 | 115 | 0 | 0 | 0 | 0
Total downtine due to high water usage | 20 | 89 | 46 | 18 | 0 | 0 | 0
Annual Downtime Hours (hr) | 3808 | 1433 | 161 | 18 | 0 | 0 | 0
Reduction in chiller load (%) | 56.5183 | 83.5046 | 98.0365 | 99.7945 | 100 | 100 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 6366.8571 | 9420.4286 | 11055.8571 | 11239.7143 | 11262.8571 | 11262.8571 | 11262.8571
water used for pre-cooling in Uravu (m³/MW/year) | 980.8457 | 1460.4171 | 1499.0657 | 1071.9771 | 1316.0829 | 0 | 0
Water used for cooling faciltiy water (m³/MW/year) | 0.89388 | 9.8204 | 9.9061 | 0.53878 | 0 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 5385.1176 | 7950.191 | 9546.8853 | 10167.1984 | 9946.7743 | 11262.8571 | 11262.8571
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 5498 | 7271 | 8303 | 8678 | 8758 | 8760 | 8760
Hours Air-cooled Chiller Required | 3262 | 1489 | 457 | 82 | 2 | 0 | 0
Electricity Cost ($) | 266948.6667 | 164705.6667 | 105193.6667 | 83568.6667 | 78955.3333 | 78840 | 78840
Total annualized cost (Uravu + Air cooled chiller ($/MW) | 380564.1667 | 246119.4444 | 174004.1667 | 165786.6667 | 164766.6667 | 164766.6667 | 164766.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 309448.6667 | 207205.6667 | 147693.6667 | 126068.6667 | 121455.3333 | 87506.6667 | 87506.6667
Total avoided cost (Air-cooled chiller($/MW)) | 617833.3333 | 617833.3333 | 617833.3333 | 617833.3333 | 617833.3333 | 617833.3333 | 617833.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 92853.3333 | 116603.3333 | 129323.3333 | 130753.3333 | 130933.3333 | 130933.3333 | 130933.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | 71115.5 | 38913.7778 | 26310.5 | 39718 | 43311.3333 | 77260 | 77260
Net cost allocated to water (Air-cooled chiller) | -237269.1667 | -371713.8889 | -443829.1667 | -452046.6667 | -453066.6667 | -453066.6667 | -453066.6667
NVW (Gross Production) | 14.5839 | 12.3777 | 11.6973 | 11.6332 | 11.6252 | 11.6252 | 11.6252
NVW (Net Delivered, No Credit) | 17.2426 | 14.6667 | 13.5461 | 12.8603 | 13.1634 | 11.6252 | 11.6252
Fair NVW (Dry cooler + Air cooled chiller) | 13.2059 | 4.8947 | 2.7559 | 3.9065 | 4.3543 | 6.8597 | 6.8597
Fair NVW (Air cooled chiller) | -44.0602 | -46.7553 | -46.4894 | -44.4613 | -45.5491 | -40.2266 | -40.2266
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 1516936.7133 | 844763.8889 | 484187.5 | 443100 | 438000 | 438000 | 438000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 1334743.3333 | 823528.3333 | 525968.3333 | 417843.3333 | 394776.6667 | 394200 | 394200
PUE_uravu | 1.1732 | 1.0964 | 1.0553 | 1.0506 | 1.05 | 1.05 | 1.05
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.1524 | 1.094 | 1.06 | 1.0477 | 1.0451 | 1.045 | 1.045
WUE | -0.61474 | -0.90756 | -1.0898 | -1.1606 | -1.1355 | -1.2857 | -1.2857
Grid CO₂ (kg/kWh) | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
Grid water (L/kWh) | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Uravu water foot print (m3/year) | 3792.3418 | 2111.9097 | 1210.4688 | 1107.75 | 1095 | 1095 | 1095
Uravu CO2 emission (tCO₂/yr) | 530.9278 | 295.6674 | 169.4656 | 155.085 | 153.3 | 153.3 | 153.3
Cooling tower + Air cooled chiller mixed mode analysis
Variable | Value | Value | Value | Value | Value | Value | Value
Hours Cooling is Sufficient | 7212 | 8598 | 8760 | 8760 | 8760 | 8760 | 8760
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 209531.3013 | 128566.7253 | 119103.3333 | 119103.3333 | 119103.3333 | 119103.3333 | 119103.3333
Fair NVW (Dry cooler + Air cooled chiller) | 31.7603 | 14.7862 | 5.7507 | 4.5916 | 4.5908 | 4.0543 | 4.0543
Stand-alonecooling tower + air-cooled chiller power consumption | 588120 | 139980 | 87600 | 87600 | 87600 | 87600 | 87600
PUE_Cooling_tower_chiller | 1.0671 | 1.016 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01

## Madrid
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-waste heat system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
CAPEX ($) | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286
Rated Power (Normal Operation) (kW) | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958
Rated Power (with Pre-Cooling) (kW) | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458
Uravu electrical consumption (kWh) | 20186.933 | 34301.8342 | 43764.8327 | 44585.3378 | 44780.4076 | 44923.6874 | 44939.1248
System Downtime Trigger (WBT) (deg C) | 9.5 | 14.5 | 19.5 | 24.5 | 29.5 | 34.5 | 39.5
Vapor Temperature (deg C) | 12.5 | 17.5 | 22.5 | 27.5 | 32.5 | 37.5 | 42.5
Facility water outlet temperature (deg C) | 23.5 | 28.5 | 33.5 | 38.5 | 43.5 | 48.5 | 53.5
Hours evaporative cooler is operational for facility water | 31 | 311 | 832 | 352 | 30 | 0 | 0
Hours chiller is operational for facility water cooling | 2 | 129 | 572 | 148 | 3 | 0 | 0
Total downtime due to WBT trigger | 4781 | 1959 | 126 | 0 | 0 | 0 | 0
Total downtine due to high water usage | 56 | 135 | 110 | 70 | 31 | 3 | 0
Annual Downtime Hours (hr) | 4837 | 2094 | 236 | 70 | 31 | 3 | 0
Reduction in chiller load (%) | 44.7603 | 74.6233 | 90.7763 | 97.5114 | 99.6119 | 99.9658 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 5043.8571 | 8570.5714 | 10959.4286 | 11172.8571 | 11223 | 11259 | 11262.8571
water used for pre-cooling in Uravu (m³/MW/year) | 1447.9457 | 2549.6486 | 2668.8343 | 1614.9857 | 1403.4857 | 1232.9743 | 188.1
Water used for cooling faciltiy water (m³/MW/year) | 5.7184 | 63.9184 | 195.7959 | 71.6694 | 5.3755 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 3590.1931 | 5957.0045 | 8094.7984 | 9486.202 | 9814.1388 | 10026.0257 | 11074.7571
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 4077 | 5842 | 7143 | 7953 | 8539 | 8751 | 8760
Hours Air-cooled Chiller Required | 4683 | 2918 | 1617 | 807 | 221 | 9 | 0
Electricity Cost ($) | 314003.7 | 222400.2 | 154878.3 | 112839.3 | 82425.9 | 71423.1 | 70956
Total annualized cost (Uravu + Air cooled chiller ($/MW) | 402704.6667 | 264530.9167 | 177950.1667 | 161621.1667 | 157604.4167 | 156159.6667 | 156006.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 356503.7 | 264900.2 | 197378.3 | 155339.3 | 124925.9 | 113923.1 | 79622.6667
Total avoided cost (Air-cooled chiller($/MW)) | 559433.3333 | 559433.3333 | 559433.3333 | 559433.3333 | 559433.3333 | 559433.3333 | 559433.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 78640.3333 | 103327.3333 | 120049.3333 | 121543.3333 | 121894.3333 | 122146.3333 | 122173.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | 46200.9667 | -369.2833 | -19428.1333 | 6281.8667 | 32678.5167 | 42236.5667 | 76384
Net cost allocated to water (Air-cooled chiller) | -156728.6667 | -294902.4167 | -381483.1667 | -397812.1667 | -401828.9167 | -403273.6667 | -403426.6667
NVW (Gross Production) | 15.5913 | 12.0561 | 10.954 | 10.8784 | 10.8611 | 10.8488 | 10.8475
NVW (Net Delivered, No Credit) | 21.9042 | 17.3455 | 14.8304 | 12.8126 | 12.4203 | 12.1829 | 11.0317
Fair NVW (Dry cooler + Air cooled chiller) | 12.8687 | -0.061991 | -2.4001 | 0.66221 | 3.3297 | 4.2127 | 6.8971
Fair NVW (Air cooled chiller) | -43.6547 | -49.5052 | -47.127 | -41.9359 | -40.9439 | -40.2227 | -36.4276
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 1808544.4444 | 1040912.5 | 559908.3333 | 469191.6667 | 446876.3889 | 438850 | 438000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 1744465 | 1235556.6667 | 860435 | 626885 | 457921.6667 | 396795 | 394200
PUE_uravu | 1.2065 | 1.1188 | 1.0639 | 1.0536 | 1.051 | 1.0501 | 1.05
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.1991 | 1.141 | 1.0982 | 1.0716 | 1.0523 | 1.0453 | 1.045
WUE | -0.40984 | -0.68002 | -0.92406 | -1.0829 | -1.1203 | -1.1445 | -1.2642
Grid CO₂ (kg/kWh) | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108
Grid water (L/kWh) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8
Uravu water foot print (m3/year) | 3255.38 | 1873.6425 | 1007.835 | 844.545 | 804.3775 | 789.93 | 788.4
Uravu CO2 emission (tCO₂/yr) | 195.3228 | 112.4185 | 60.4701 | 50.6727 | 48.2627 | 47.3958 | 47.304
Cooling tower + Air cooled chiller mixed mode analysis
Variable | Value | Value | Value | Value | Value | Value | Value
Hours Cooling is Sufficient | 6549 | 8557 | 8760 | 8760 | 8760 | 8760 | 8760
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 220750.7067 | 112922.3115 | 102021.3333 | 102021.3333 | 102021.3333 | 102021.3333 | 102021.3333
Fair NVW (Dry cooler + Air cooled chiller) | 50.6808 | 25.4505 | 9.38 | 6.2828 | 5.6636 | 5.3998 | 4.8746
Stand-alonecooling tower + air-cooled chiller power consumption | 802490 | 153236.6667 | 87600 | 87600 | 87600 | 87600 | 87600
PUE_Cooling_tower_chiller | 1.0916 | 1.0175 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01

## London
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-waste heat system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
CAPEX ($) | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286
Rated Power (Normal Operation) (kW) | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958
Rated Power (with Pre-Cooling) (kW) | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458
Uravu electrical consumption (kWh) | 26017.1128 | 39514.5192 | 44000.5218 | 44529.1009 | 44552.423 | 44552.423 | 44552.423
System Downtime Trigger (WBT) (deg C) | 9.5 | 14.5 | 19.5 | 24.5 | 29.5 | 34.5 | 39.5
Vapor Temperature (deg C) | 12.5 | 17.5 | 22.5 | 27.5 | 32.5 | 37.5 | 42.5
Facility water outlet temperature (deg C) | 23.5 | 28.5 | 33.5 | 38.5 | 43.5 | 48.5 | 53.5
Hours evaporative cooler is operational for facility water | 3 | 2 | 15 | 0 | 0 | 0 | 0
Hours chiller is operational for facility water cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total downtime due to WBT trigger | 3666 | 1042 | 73 | 0 | 0 | 0 | 0
Total downtine due to high water usage | 38 | 39 | 50 | 5 | 0 | 0 | 0
Annual Downtime Hours (hr) | 3704 | 1081 | 123 | 5 | 0 | 0 | 0
Reduction in chiller load (%) | 57.7169 | 87.6598 | 98.5959 | 99.9429 | 100 | 100 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 6500.5714 | 9873 | 11104.7143 | 11256.4286 | 11262.8571 | 11262.8571 | 11262.8571
water used for pre-cooling in Uravu (m³/MW/year) | 545.0914 | 606.3686 | 1187.5886 | 542.4943 | 1.5429 | 0 | 0
Water used for cooling faciltiy water (m³/MW/year) | 0.2449 | 0 | 1.9837 | 0 | 0 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 5955.2351 | 9266.6314 | 9915.142 | 10713.9343 | 11261.3143 | 11262.8571 | 11262.8571
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 6359 | 8039 | 8595 | 8752 | 8760 | 8760 | 8760
Hours Air-cooled Chiller Required | 2401 | 721 | 165 | 8 | 0 | 0 | 0
Electricity Cost ($) | 217297.6667 | 120417.6667 | 88355 | 79301.3333 | 78840 | 78840 | 78840
Total annualized cost (Uravu + Air cooled chiller ($/MW) | 374660 | 226023.3333 | 171736.6667 | 165050 | 164766.6667 | 164766.6667 | 164766.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 259797.6667 | 162917.6667 | 130855 | 121801.3333 | 87506.6667 | 87506.6667 | 87506.6667
Total avoided cost (Air-cooled chiller($/MW)) | 617833.3333 | 617833.3333 | 617833.3333 | 617833.3333 | 617833.3333 | 617833.3333 | 617833.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 93893.3333 | 120123.3333 | 129703.3333 | 130883.3333 | 130933.3333 | 130933.3333 | 130933.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | 114862.3333 | 63105.6667 | 40881.6667 | 43248.6667 | 77260 | 77260 | 77260
Net cost allocated to water (Air-cooled chiller) | -243173.3333 | -391810 | -446096.6667 | -452783.3333 | -453066.6667 | -453066.6667 | -453066.6667
NVW (Gross Production) | 14.4439 | 12.1669 | 11.68 | 11.6274 | 11.6252 | 11.6252 | 11.6252
NVW (Net Delivered, No Credit) | 15.7665 | 12.963 | 13.0813 | 12.2162 | 11.6268 | 11.6252 | 11.6252
Fair NVW (Dry cooler + Air cooled chiller) | 19.2876 | 6.81 | 4.1232 | 4.0367 | 6.8607 | 6.8597 | 6.8597
Fair NVW (Air cooled chiller) | -40.8335 | -42.2818 | -44.9915 | -42.2612 | -40.2321 | -40.2266 | -40.2266
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 1487466.6667 | 744283.3333 | 472850 | 439416.6667 | 438000 | 438000 | 438000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 1086488.3333 | 602088.3333 | 441775 | 396506.6667 | 394200 | 394200 | 394200
PUE_uravu | 1.1698 | 1.085 | 1.054 | 1.0502 | 1.05 | 1.05 | 1.05
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.124 | 1.0687 | 1.0504 | 1.0453 | 1.045 | 1.045 | 1.045
WUE | -0.67982 | -1.0578 | -1.1319 | -1.2231 | -1.2855 | -1.2857 | -1.2857
Grid CO₂ (kg/kWh) | 0.19 | 0.19 | 0.19 | 0.19 | 0.19 | 0.19 | 0.19
Grid water (L/kWh) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
Uravu water foot print (m3/year) | 2231.2 | 1116.425 | 709.275 | 659.125 | 657 | 657 | 657
Uravu CO2 emission (tCO₂/yr) | 282.6187 | 141.4138 | 89.8415 | 83.4892 | 83.22 | 83.22 | 83.22
Cooling tower + Air cooled chiller mixed mode analysis
Variable | Value | Value | Value | Value | Value | Value | Value
Hours Cooling is Sufficient | 7514 | 8653 | 8760 | 8760 | 8760 | 8760 | 8760
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 173104.6693 | 103721.3453 | 97203.3333 | 97203.3333 | 97203.3333 | 97203.3333 | 97203.3333
Fair NVW (Dry cooler + Air cooled chiller) | 33.8451 | 13.1981 | 7.5171 | 6.3326 | 5.9996 | 5.9988 | 5.9988
Stand-alonecooling tower + air-cooled chiller power consumption | 490473.3333 | 122196.6667 | 87600 | 87600 | 87600 | 87600 | 87600
PUE_Cooling_tower_chiller | 1.056 | 1.0139 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01

## Stockholm
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-waste heat system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
CAPEX ($) | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286
Rated Power (Normal Operation) (kW) | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958
Rated Power (with Pre-Cooling) (kW) | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458
Uravu electrical consumption (kWh) | 30257.2435 | 39761.0469 | 44103.5199 | 44562.603 | 44595.4144 | 44599.7579 | 44599.7579
System Downtime Trigger (WBT) (deg C) | 9.5 | 14.5 | 19.5 | 24.5 | 29.5 | 34.5 | 39.5
Vapor Temperature (deg C) | 12.5 | 17.5 | 22.5 | 27.5 | 32.5 | 37.5 | 42.5
Facility water outlet temperature (deg C) | 23.5 | 28.5 | 33.5 | 38.5 | 43.5 | 48.5 | 53.5
Hours evaporative cooler is operational for facility water | 2 | 24 | 29 | 4 | 0 | 0 | 0
Hours chiller is operational for facility water cooling | 0 | 6 | 2 | 0 | 0 | 0 | 0
Total downtime due to WBT trigger | 2845 | 978 | 82 | 0 | 0 | 0 | 0
Total downtine due to high water usage | 35 | 54 | 28 | 8 | 1 | 0 | 0
Annual Downtime Hours (hr) | 2880 | 1032 | 110 | 8 | 1 | 0 | 0
Reduction in chiller load (%) | 67.1233 | 88.1507 | 98.7215 | 99.9087 | 99.9886 | 100 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 7560 | 9936 | 11121.4286 | 11252.5714 | 11261.5714 | 11262.8571 | 11262.8571
water used for pre-cooling in Uravu (m³/MW/year) | 677.1343 | 1078.2257 | 622.6971 | 1077.3771 | 259.5086 | 0 | 0
Water used for cooling faciltiy water (m³/MW/year) | 0.12245 | 4.5796 | 4.7878 | 0.8449 | 0 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 6882.7433 | 8853.1947 | 10493.9437 | 10174.3494 | 11002.0629 | 11262.8571 | 11262.8571
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 6187 | 7744 | 8521 | 8728 | 8757 | 8760 | 8760
Hours Air-cooled Chiller Required | 2573 | 1016 | 239 | 32 | 3 | 0 | 0
Electricity Cost ($) | 170412.25 | 103072 | 69466.75 | 60514 | 59259.75 | 59130 | 59130
Total annualized cost (Uravu + Air cooled chiller ($/MW) | 265266.6667 | 186776.25 | 147551.6667 | 143206.6667 | 142909.1667 | 142866.6667 | 142866.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 212912.25 | 145572 | 111966.75 | 103014 | 101759.75 | 67796.6667 | 67796.6667
Total avoided cost (Air-cooled chiller($/MW)) | 471833.3333 | 471833.3333 | 471833.3333 | 471833.3333 | 471833.3333 | 471833.3333 | 471833.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 87433.3333 | 101293.3333 | 108208.3333 | 108973.3333 | 109025.8333 | 109033.3333 | 109033.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | 52354.4167 | 41204.25 | 35584.9167 | 40192.6667 | 41149.4167 | 75070 | 75070
Net cost allocated to water (Air-cooled chiller) | -206566.6667 | -285057.0833 | -324281.6667 | -328626.6667 | -328924.1667 | -328966.6667 | -328966.6667
NVW (Gross Production) | 11.5653 | 10.1946 | 9.7297 | 9.6843 | 9.6812 | 9.6808 | 9.6808
NVW (Net Delivered, No Credit) | 12.7033 | 11.4414 | 10.3115 | 10.7106 | 9.9096 | 9.6808 | 9.6808
Fair NVW (Dry cooler + Air cooled chiller) | 7.6066 | 4.6542 | 3.391 | 3.9504 | 3.7402 | 6.6653 | 6.6653
Fair NVW (Air cooled chiller) | -30.0123 | -32.1982 | -30.9018 | -32.2995 | -29.8966 | -29.2081 | -29.2081
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 1254000 | 730730.5556 | 469233.3333 | 440266.6667 | 438283.3333 | 438000 | 438000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 1136081.6667 | 687146.6667 | 463111.6667 | 403426.6667 | 395065 | 394200 | 394200
PUE_uravu | 1.1432 | 1.0834 | 1.0536 | 1.0503 | 1.05 | 1.05 | 1.05
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.1297 | 1.0784 | 1.0529 | 1.0461 | 1.0451 | 1.045 | 1.045
WUE | -0.7857 | -1.0106 | -1.1979 | -1.1615 | -1.2559 | -1.2857 | -1.2857
Grid CO₂ (kg/kWh) | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013
Grid water (L/kWh) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Uravu water foot print (m3/year) | 627 | 365.3653 | 234.6167 | 220.1333 | 219.1417 | 219 | 219
Uravu CO2 emission (tCO₂/yr) | 16.302 | 9.4995 | 6.1 | 5.7235 | 5.6977 | 5.694 | 5.694
Cooling tower + Air cooled chiller mixed mode analysis
Variable | Value | Value | Value | Value | Value | Value | Value
Hours Cooling is Sufficient | 7588 | 8637 | 8759 | 8760 | 8760 | 8760 | 8760
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 140296.0301 | 80556.1095 | 73608.2827 | 73551.3333 | 73551.3333 | 73551.3333 | 73551.3333
Fair NVW (Dry cooler + Air cooled chiller) | 18.1571 | 11.9979 | 7.0463 | 6.8462 | 6.3041 | 6.1543 | 6.1543
Stand-alonecooling tower + air-cooled chiller power consumption | 466546.6667 | 127370 | 87923.3333 | 87600 | 87600 | 87600 | 87600
PUE_Cooling_tower_chiller | 1.0533 | 1.0145 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01

## Hyderabad
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-waste heat system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
CAPEX ($) | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286
Rated Power (Normal Operation) (kW) | 4.0935 | 4.0935 | 4.0935 | 4.0935 | 4.0935 | 4.0935 | 4.0935
Rated Power (with Pre-Cooling) (kW) | 4.3435 | 4.3435 | 4.3435 | 4.3435 | 4.3435 | 4.3435 | 4.3435
Uravu electrical consumption (kWh) | 61.7495 | 2125.2112 | 13294.6304 | 37168.6269 | 39347.2116 | 39606.9637 | 39805.2985
System Downtime Trigger (WBT) (deg C) | 9.5 | 14.5 | 19.5 | 24.5 | 29.5 | 34.5 | 39.5
Vapor Temperature (deg C) | 12.5 | 17.5 | 22.5 | 27.5 | 32.5 | 37.5 | 42.5
Facility water outlet temperature (deg C) | 23.5 | 28.5 | 33.5 | 38.5 | 43.5 | 48.5 | 53.5
Hours evaporative cooler is operational for facility water | 2 | 67 | 767 | 1098 | 310 | 0 | 0
Hours chiller is operational for facility water cooling | 1 | 39 | 419 | 630 | 96 | 0 | 0
Total downtime due to WBT trigger | 8747 | 8326 | 5933 | 245 | 0 | 0 | 0
Total downtine due to high water usage | 1 | 21 | 114 | 348 | 99 | 44 | 0
Annual Downtime Hours (hr) | 8748 | 8347 | 6047 | 593 | 99 | 44 | 0
Reduction in chiller load (%) | 0.12557 | 4.2694 | 26.1872 | 86.0388 | 97.774 | 99.4977 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 15.4286 | 531 | 3488.1429 | 10500.4286 | 11135.5714 | 11206.2857 | 11262.8571
water used for pre-cooling in Uravu (m³/MW/year) | 13.4486 | 313.4829 | 2089.9029 | 4862.6486 | 2268.0257 | 967.0886 | 775.44
Water used for cooling faciltiy water (m³/MW/year) | 0.51429 | 14.1429 | 171.551 | 240.7592 | 62.0571 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 1.4657 | 203.3743 | 1226.689 | 5397.0208 | 8805.4886 | 10239.1971 | 10487.4171
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 13 | 359 | 1824 | 5595 | 7829 | 8574 | 8760
Hours Air-cooled Chiller Required | 8747 | 8401 | 6936 | 3165 | 931 | 186 | 0
Electricity Cost ($) | 291625.1667 | 281648.8333 | 239408 | 130677.5 | 66263.8333 | 44783 | 39420
Total annualized cost (Uravu + Air cooled chiller ($/MW) | 368832.6389 | 357825.4167 | 296172.3611 | 143434.1667 | 124253.0556 | 122213.3333 | 120966.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 334125.1667 | 324148.8333 | 281908 | 173177.5 | 108763.8333 | 87283 | 48086.6667
Total avoided cost (Air-cooled chiller($/MW)) | 325833.3333 | 325833.3333 | 325833.3333 | 325833.3333 | 325833.3333 | 325833.3333 | 325833.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 43393.3333 | 45398.3333 | 56898.3333 | 84168.3333 | 86638.3333 | 86913.3333 | 87133.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | 34707.4722 | 33676.5833 | 14264.3611 | -29743.3333 | 15489.2222 | 34930.3333 | 72880
Net cost allocated to water (Air-cooled chiller) | 42999.3056 | 31992.0833 | -29660.9722 | -182399.1667 | -201580.2778 | -203620 | -204866.6667
NVW (Gross Production) | 2812.5309 | 85.4959 | 16.3119 | 8.0157 | 7.7803 | 7.7558 | 7.7363
NVW (Net Delivered, No Credit) | 29605.588 | 223.2255 | 46.3837 | 15.5953 | 9.8391 | 8.4883 | 8.3084
Fair NVW (Dry cooler + Air cooled chiller) | 23679.5619 | 165.5892 | 11.6283 | -5.5111 | 1.759 | 3.4114 | 6.9493
Fair NVW (Air cooled chiller) | 29336.7582 | 157.3064 | -24.1797 | -33.7963 | -22.8926 | -19.8863 | -19.5345
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 2916659.7222 | 2806587.5 | 2190056.9444 | 662675 | 470863.8889 | 450466.6667 | 438000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 2916251.6667 | 2816488.3333 | 2394080 | 1306775 | 662638.3333 | 447830 | 394200
PUE_uravu | 1.333 | 1.3204 | 1.25 | 1.0756 | 1.0538 | 1.0514 | 1.05
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.3329 | 1.3215 | 1.2733 | 1.1492 | 1.0756 | 1.0511 | 1.045
WUE | -0.00016732 | -0.023216 | -0.14003 | -0.6161 | -1.0052 | -1.1689 | -1.1972
Grid CO₂ (kg/kWh) | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73
Grid water (L/kWh) | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
Uravu water foot print (m3/year) | 6708.3174 | 6455.1512 | 5037.131 | 1524.1525 | 1082.9869 | 1036.0733 | 1007.4
Uravu CO2 emission (tCO₂/yr) | 2129.1616 | 2048.8089 | 1598.7416 | 483.7528 | 343.7306 | 328.8407 | 319.74
Cooling tower + Air cooled chiller mixed mode analysis
Variable | Value | Value | Value | Value | Value | Value | Value
Hours Cooling is Sufficient | 328 | 2502 | 8179 | 8760 | 8760 | 8760 | 8760
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 328881.1893 | 262937.2473 | 90736.8063 | 73113.3333 | 73113.3333 | 73113.3333 | 73113.3333
Fair NVW (Dry cooler + Air cooled chiller) | 27257.3243 | 466.5692 | 167.4716 | 13.0296 | 5.8077 | 4.7953 | 4.5629
Stand-alonecooling tower + air-cooled chiller power consumption | 2813946.6667 | 2111020 | 275456.6667 | 87600 | 87600 | 87600 | 87600
PUE_Cooling_tower_chiller | 1.3212 | 1.241 | 1.0314 | 1.01 | 1.01 | 1.01 | 1.01

## Bengaluru
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-waste heat system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095
CAPEX ($) | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286
Rated Power (Normal Operation) (kW) | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958
Rated Power (with Pre-Cooling) (kW) | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458
Uravu electrical consumption (kWh) | 0 | 1595.1948 | 18509.4945 | 38577.7262 | 39387.3049 | 39528.5099 | 39528.5099
System Downtime Trigger (WBT) (deg C) | 9.5 | 14.5 | 19.5 | 24.5 | 29.5 | 34.5 | 39.5
Vapor Temperature (deg C) | 12.5 | 17.5 | 22.5 | 27.5 | 32.5 | 37.5 | 42.5
Facility water outlet temperature (deg C) | 23.5 | 28.5 | 33.5 | 38.5 | 43.5 | 48.5 | 53.5
Hours evaporative cooler is operational for facility water | 0 | 121 | 627 | 260 | 1 | 0 | 0
Hours chiller is operational for facility water cooling | 0 | 81 | 322 | 38 | 0 | 0 | 0
Total downtime due to WBT trigger | 8760 | 8435 | 4629 | 45 | 2 | 0 | 0
Total downtine due to high water usage | 0 | 15 | 181 | 163 | 27 | 0 | 0
Annual Downtime Hours (hr) | 8760 | 8450 | 4810 | 208 | 29 | 0 | 0
Reduction in chiller load (%) | 0 | 2.6142 | 41.4155 | 97.1918 | 99.6689 | 100 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 0 | 398.5714 | 5078.5714 | 10995.4286 | 11225.5714 | 11262.8571 | 11262.8571
water used for pre-cooling in Uravu (m³/MW/year) | 0 | 295.7143 | 2479.7829 | 2940.12 | 1295.82 | 1176.7886 | 0
Water used for cooling faciltiy water (m³/MW/year) | 0 | 28.5061 | 135.8816 | 46.2245 | 0.2449 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 0 | 74.351 | 2462.9069 | 8009.0841 | 9929.5065 | 10086.0686 | 11262.8571
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 1 | 427 | 4232 | 7534 | 8641 | 8760 | 8760
Hours Air-cooled Chiller Required | 8759 | 8333 | 4528 | 1226 | 119 | 0 | 0
Electricity Cost ($) | 277372.6083 | 265703.7583 | 161478.4667 | 71031.1833 | 40708.6083 | 37449 | 37449
Total annualized cost (Uravu + Air cooled chiller ($/MW) | 354566.6667 | 346888.9514 | 250784.9722 | 124554.5139 | 119557.25 | 118776.6667 | 118776.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 319872.6083 | 308203.7583 | 203978.4667 | 113531.1833 | 83208.6083 | 46115.6667 | 46115.6667
Total avoided cost (Air-cooled chiller($/MW)) | 311233.3333 | 311233.3333 | 311233.3333 | 311233.3333 | 311233.3333 | 311233.3333 | 311233.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 43333.3333 | 44805.8333 | 62095.8333 | 83955.3333 | 84805.5833 | 84943.3333 | 84943.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | 34694.0583 | 38685.1931 | 46806.5056 | 11023.3306 | 36348.6417 | 72661 | 72661
Net cost allocated to water (Air-cooled chiller) | 43333.3333 | 35655.6181 | -60448.3611 | -186678.8194 | -191676.0833 | -192456.6667 | -192456.6667
NVW (Gross Production) | 0 | 112.4161 | 12.227 | 7.6355 | 7.5547 | 7.5419 | 7.5419
NVW (Net Delivered, No Credit) | 0 | 602.6257 | 25.2124 | 10.4825 | 8.5408 | 8.4218 | 7.5419
Fair NVW (Dry cooler + Air cooled chiller) | 0 | 520.3048 | 19.0046 | 1.3764 | 3.6607 | 7.2041 | 6.4514
Fair NVW (Air cooled chiller) | 0 | 479.5579 | -24.5435 | -23.3084 | -19.3037 | -19.0814 | -17.0877
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 2920000 | 2839181.9444 | 1827561.1111 | 498819.4444 | 446216.6667 | 438000 | 438000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 2919711.6667 | 2796881.6667 | 1699773.3333 | 747696.6667 | 428511.6667 | 394200 | 394200
PUE_uravu | 1.3333 | 1.3241 | 1.2086 | 1.0569 | 1.0509 | 1.05 | 1.05
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.3333 | 1.3193 | 1.194 | 1.0854 | 1.0489 | 1.045 | 1.045
WUE | 0 | -0.0084876 | -0.28115 | -0.91428 | -1.1335 | -1.1514 | -1.2857
Grid CO₂ (kg/kWh) | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71
Grid water (L/kWh) | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
Uravu water foot print (m3/year) | 6716 | 6530.1185 | 4203.3906 | 1147.2847 | 1026.2983 | 1007.4 | 1007.4
Uravu CO2 emission (tCO₂/yr) | 2073.2 | 2015.8192 | 1297.5684 | 354.1618 | 316.8138 | 310.98 | 310.98
Cooling tower + Air cooled chiller mixed mode analysis
Variable | Value | Value | Value | Value | Value | Value | Value
Hours Cooling is Sufficient | 160 | 3375 | 8681 | 8758 | 8760 | 8760 | 8760
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 319555.9433 | 225625.3781 | 70603.425 | 68353.766 | 68295.3333 | 68295.3333 | 68295.3333
Fair NVW (Dry cooler + Air cooled chiller) |  |  |  | 7.0171 | 5.1626 | 5.0051 | 4.4821
Stand-alonecooling tower + air-cooled chiller power consumption | 2868266.6667 | 1828750 | 113143.3333 | 88246.6667 | 87600 | 87600 | 87600
PUE_Cooling_tower_chiller | 1.3274 | 1.2088 | 1.0129 | 1.0101 | 1.01 | 1.01 | 1.01

## Mumbai
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-waste heat system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.083 | 0.083 | 0.083 | 0.083 | 0.083 | 0.083 | 0.083
CAPEX ($) | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286
Rated Power (Normal Operation) (kW) | 4.0935 | 4.0935 | 4.0935 | 4.0935 | 4.0935 | 4.0935 | 4.0935
Rated Power (with Pre-Cooling) (kW) | 4.3435 | 4.3435 | 4.3435 | 4.3435 | 4.3435 | 4.3435 | 4.3435
Uravu electrical consumption (kWh) | 0 | 380.7884 | 6051.9592 | 19699.0549 | 38089.2569 | 38445.4242 | 38445.4242
System Downtime Trigger (WBT) (deg C) | 9.5 | 14.5 | 19.5 | 24.5 | 29.5 | 34.5 | 39.5
Vapor Temperature (deg C) | 12.5 | 17.5 | 22.5 | 27.5 | 32.5 | 37.5 | 42.5
Facility water outlet temperature (deg C) | 23.5 | 28.5 | 33.5 | 38.5 | 43.5 | 48.5 | 53.5
Hours evaporative cooler is operational for facility water | 0 | 11 | 135 | 202 | 2 | 0 | 0
Hours chiller is operational for facility water cooling | 0 | 3 | 19 | 20 | 0 | 0 | 0
Total downtime due to WBT trigger | 8760 | 8681 | 7353 | 4066 | 17 | 0 | 0
Total downtine due to high water usage | 0 | 5 | 99 | 247 | 65 | 0 | 0
Annual Downtime Hours (hr) | 8760 | 8686 | 7452 | 4313 | 82 | 0 | 0
Reduction in chiller load (%) | 0 | 0.8105 | 14.7146 | 50.5365 | 99.0639 | 100 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 0 | 95.1429 | 1681.7143 | 5717.5714 | 11157.4286 | 11262.8571 | 11262.8571
water used for pre-cooling in Uravu (m³/MW/year) | 0 | 62.64 | 916.8171 | 2389.3457 | 1612.3629 | 379.3371 | 0
Water used for cooling faciltiy water (m³/MW/year) | 0 | 2.0082 | 24.1592 | 27.8327 | 0.17143 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 0 | 30.4947 | 740.738 | 3300.3931 | 9544.8943 | 10883.52 | 11262.8571
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 0 | 92 | 1130 | 5183 | 8560 | 8760 | 8760
Hours Air-cooled Chiller Required | 8760 | 8668 | 7630 | 3577 | 200 | 0 | 0
Electricity Cost ($) | 242360 | 240158.2867 | 215317.2167 | 118322.1717 | 37504.9333 | 32718.6 | 32718.6
Total annualized cost (Uravu + Air cooled chiller ($/MW) | 319526.6667 | 317796.4625 | 288860.8181 | 215035.4306 | 115449.0333 | 113520.6667 | 113520.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 276193.3333 | 282658.2867 | 257817.2167 | 160822.1717 | 80004.9333 | 41385.2667 | 41385.2667
Total avoided cost (Air-cooled chiller($/MW)) | 276193.3333 | 276193.3333 | 276193.3333 | 276193.3333 | 276193.3333 | 276193.3333 | 276193.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 43333.3333 | 43640.4333 | 48761.5333 | 61788.3833 | 79347.0333 | 79687.3333 | 79687.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | 43333.3333 | 35138.1758 | 31043.6014 | 54213.2589 | 35444.1 | 72135.4 | 72135.4
Net cost allocated to water (Air-cooled chiller) | 43333.3333 | 41603.1292 | 12667.4847 | -61157.9028 | -160744.3 | -162672.6667 | -162672.6667
NVW (Gross Production) | 0 | 458.6832 | 28.9951 | 10.8068 | 7.1116 | 7.0752 | 7.0752
NVW (Net Delivered, No Credit) | 0 | 1431.0828 | 65.8283 | 18.7215 | 8.313 | 7.3218 | 7.0752
Fair NVW (Dry cooler + Air cooled chiller) | 0 | 1152.2718 | 41.909 | 16.4263 | 3.7134 | 6.6279 | 6.4047
Fair NVW (Air cooled chiller) | 0 | 1364.2744 | 17.1012 | -18.5305 | -16.8409 | -14.9467 | -14.4433
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 2920000 | 2899154.1667 | 2550531.9444 | 1661069.4444 | 461233.3333 | 438000 | 438000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 2920000 | 2893473.3333 | 2594183.3333 | 1425568.3333 | 451866.6667 | 394200 | 394200
PUE_uravu | 1.3333 | 1.331 | 1.2912 | 1.1896 | 1.0527 | 1.05 | 1.05
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.3333 | 1.3303 | 1.2961 | 1.1627 | 1.0516 | 1.045 | 1.045
WUE | 0 | -0.0034811 | -0.084559 | -0.37676 | -1.0896 | -1.2424 | -1.2857
Grid CO₂ (kg/kWh) | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73
Grid water (L/kWh) | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
Uravu water foot print (m3/year) | 6716 | 6668.0546 | 5866.2235 | 3820.4597 | 1060.8367 | 1007.4 | 1007.4
Uravu CO2 emission (tCO₂/yr) | 2131.6 | 2116.3825 | 1861.8883 | 1212.5807 | 336.7003 | 319.74 | 319.74
Cooling tower + Air cooled chiller mixed mode analysis
Variable | Value | Value | Value | Value | Value | Value | Value
Hours Cooling is Sufficient | 160 | 3375 | 8681 | 8758 | 8760 | 8760 | 8760
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 289190.9097 | 289190.9097 | 287756.1583 | 258591.5743 | 178871.5664 | 61248.0339 | 60674.1333
Fair NVW (Dry cooler + Air cooled chiller) |  |  | 1.4913 | -13.1973 | -6.6447 | 4.8029 | 4.6921
Stand-alonecooling tower + air-cooled chiller power consumption | 2902216.6667 | 2540730 | 1552623.3333 | 94713.3333 | 87600 | 87600 | 87600
PUE_Cooling_tower_chiller | 1.3313 | 1.29 | 1.1772 | 1.0108 | 1.01 | 1.01 | 1.01

## New Delhi
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-waste heat system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
CAPEX ($) | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286
Rated Power (Normal Operation) (kW) | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958 | 4.8958
Rated Power (with Pre-Cooling) (kW) | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458 | 5.1458
Uravu electrical consumption (kWh) | 3689.5312 | 13234.9711 | 23068.3924 | 30925.3712 | 40619.214 | 41096.9995 | 41429.1248
System Downtime Trigger (WBT) (deg C) | 9.5 | 14.5 | 19.5 | 24.5 | 29.5 | 34.5 | 39.5
Vapor Temperature (deg C) | 12.5 | 17.5 | 22.5 | 27.5 | 32.5 | 37.5 | 42.5
Facility water outlet temperature (deg C) | 23.5 | 28.5 | 33.5 | 38.5 | 43.5 | 48.5 | 53.5
Hours evaporative cooler is operational for facility water | 11 | 204 | 667 | 874 | 368 | 10 | 0
Hours chiller is operational for facility water cooling | 1 | 71 | 449 | 599 | 174 | 0 | 0
Total downtime due to WBT trigger | 8039 | 6124 | 4058 | 2274 | 2 | 0 | 0
Total downtine due to high water usage | 4 | 64 | 106 | 133 | 178 | 70 | 0
Annual Downtime Hours (hr) | 8043 | 6188 | 4164 | 2407 | 180 | 70 | 0
Reduction in chiller load (%) | 8.1735 | 28.5502 | 47.3402 | 65.6849 | 95.9589 | 99.2009 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 921.8571 | 3306.8571 | 5909.1429 | 8168.1429 | 11031.4286 | 11172.8571 | 11262.8571
water used for pre-cooling in Uravu (m³/MW/year) | 215.9743 | 1287.0257 | 2452.3457 | 2722.3971 | 2705.0143 | 1177.4314 | 1302.1714
Water used for cooling faciltiy water (m³/MW/year) | 1.7633 | 38.3878 | 156.1837 | 200.6694 | 79.151 | 0.96735 | 0
Net Water Delivered to Customer (m³/MW/year) | 704.1196 | 1981.4437 | 3300.6135 | 5245.0763 | 8247.2633 | 9994.4584 | 9960.6857
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 1029 | 2151 | 3515 | 5377 | 7496 | 8502 | 8759
Hours Air-cooled Chiller Required | 7731 | 6609 | 5245 | 3383 | 1264 | 258 | 1
Electricity Cost ($) | 262330.5 | 229979.5 | 190650.8333 | 136963.1667 | 75865.3333 | 46859 | 39448.8333
Total annualized cost (Uravu + Air cooled chiller ($/MW) | 348857.0833 | 296760.1389 | 243271.8056 | 194979.5833 | 127130.5556 | 122950 | 120966.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 304830.5 | 272479.5 | 233150.8333 | 179463.1667 | 118365.3333 | 89359 | 81948.8333
Total avoided cost (Air-cooled chiller($/MW)) | 325833.3333 | 325833.3333 | 325833.3333 | 325833.3333 | 325833.3333 | 325833.3333 | 325833.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 46918.3333 | 56193.3333 | 66313.3333 | 75098.3333 | 86233.3333 | 86783.3333 | 87133.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | 44026.5833 | 24280.6389 | 10120.9722 | 15516.4167 | 8765.2222 | 33591 | 39017.8333
Net cost allocated to water (Air-cooled chiller) | 23023.75 | -29073.1944 | -82561.5278 | -130853.75 | -198702.7778 | -202883.3333 | -204866.6667
NVW (Gross Production) | 50.8954 | 16.993 | 11.2222 | 9.1941 | 7.8171 | 7.7673 | 7.7363
NVW (Net Delivered, No Credit) | 66.634 | 28.3598 | 20.0912 | 14.3179 | 10.456 | 8.6831 | 8.7477
Fair NVW (Dry cooler + Air cooled chiller) | 62.5271 | 12.254 | 3.0664 | 2.9583 | 1.0628 | 3.361 | 3.9172
Fair NVW (Air cooled chiller) | 32.6986 | -14.6727 | -25.014 | -24.9479 | -24.0932 | -20.2996 | -20.5675
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 2716904.1667 | 2195934.7222 | 1661051.3889 | 1178129.1667 | 499638.8889 | 457833.3333 | 438000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 2623305 | 2299795 | 1906508.3333 | 1369631.6667 | 758653.3333 | 468590 | 394488.3333
PUE_uravu | 1.3101 | 1.2507 | 1.1896 | 1.1345 | 1.057 | 1.0523 | 1.05
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.2995 | 1.2625 | 1.2176 | 1.1564 | 1.0866 | 1.0535 | 1.045
WUE | -0.080379 | -0.22619 | -0.37678 | -0.59875 | -0.94147 | -1.1409 | -1.1371
Grid CO₂ (kg/kWh) | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73
Grid water (L/kWh) | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
Uravu water foot print (m3/year) | 6248.8796 | 5050.6499 | 3820.4182 | 2709.6971 | 1149.1694 | 1053.0167 | 1007.4
Uravu CO2 emission (tCO₂/yr) | 1983.34 | 1603.0323 | 1212.5675 | 860.0343 | 364.7364 | 334.2183 | 319.74
Cooling tower + Air cooled chiller mixed mode analysis
Variable | Value | Value | Value | Value | Value | Value | Value
Hours Cooling is Sufficient | 2454 | 4460 | 6279 | 8749 | 8760 | 8760 | 8760
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 264699.9813 | 204102.7333 | 149154.3813 | 74540.6213 | 74208.3333 | 74208.3333 | 74208.3333
Fair NVW (Dry cooler + Air cooled chiller) ($/m3) |  | 46.7626 | 28.5151 | 22.9623 | 6.4169 | 4.8769 | 4.6943
Stand-alonecooling tower + air-cooled chiller power consumption (kwh/year) | 2126540 | 1477933.3333 | 889790 | 91156.6667 | 87600 | 87600 | 87600
PUE_Cooling_tower_chiller | 1.2428 | 1.1687 | 1.1016 | 1.0104 | 1.01 | 1.01 | 1.01

## Chennai
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-waste heat system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09
CAPEX ($) | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286
Rated Power (Normal Operation) (kW) | 4.0935 | 4.0935 | 4.0935 | 4.0935 | 4.0935 | 4.0935 | 4.0935
Rated Power (with Pre-Cooling) (kW) | 4.3435 | 4.3435 | 4.3435 | 4.3435 | 4.3435 | 4.3435 | 4.3435
Uravu electrical consumption (kWh) | 0 | 0 | 583.302 | 19912.6971 | 37165.8973 | 37994.7043 | 38056.3156
System Downtime Trigger (WBT) (deg C) | 9.5 | 14.5 | 19.5 | 24.5 | 29.5 | 34.5 | 39.5
Vapor Temperature (deg C) | 12.5 | 17.5 | 22.5 | 27.5 | 32.5 | 37.5 | 42.5
Facility water outlet temperature (deg C) | 23.5 | 28.5 | 33.5 | 38.5 | 43.5 | 48.5 | 53.5
Hours evaporative cooler is operational for facility water | 0 | 0 | 15 | 486 | 118 | 0 | 0
Hours chiller is operational for facility water cooling | 0 | 0 | 1 | 198 | 16 | 0 | 0
Total downtime due to WBT trigger | 8760 | 8760 | 8618 | 3933 | 16 | 0 | 0
Total downtine due to high water usage | 0 | 0 | 9 | 244 | 189 | 14 | 0
Annual Downtime Hours (hr) | 8760 | 8760 | 8627 | 4177 | 205 | 14 | 0
Reduction in chiller load (%) | 0 | 0 | 1.5068 | 50.0571 | 97.4772 | 99.8402 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 0 | 0 | 171 | 5892.4286 | 10999.2857 | 11244.8571 | 11262.8571
water used for pre-cooling in Uravu (m³/MW/year) | 0 | 0 | 79.1229 | 2802.4457 | 2351.8286 | 1030.5771 | 847.6457
Water used for cooling faciltiy water (m³/MW/year) | 0 | 0 | 2.5469 | 98.7306 | 20.1306 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 0 | 0 | 89.3302 | 2991.2522 | 8627.3265 | 10214.28 | 10415.2114
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 0 | 1 | 620 | 4184 | 7862 | 8704 | 8760
Hours Air-cooled Chiller Required | 8760 | 8759 | 8140 | 4576 | 898 | 56 | 0
Electricity Cost ($) | 262800 | 262774.05 | 246711 | 154225.2 | 58781.1 | 36931.2 | 35478
Total annualized cost (Uravu + Air cooled chiller ($/MW) | 339966.6667 | 339966.6667 | 336579.5417 | 224461.6667 | 121874.1667 | 116943.6667 | 116586.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 296633.3333 | 305274.05 | 289211 | 196725.2 | 101281.1 | 79431.2 | 44144.6667
Total avoided cost (Air-cooled chiller($/MW)) | 296633.3333 | 296633.3333 | 296633.3333 | 296633.3333 | 296633.3333 | 296633.3333 | 296633.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 43333.3333 | 43333.3333 | 43931.8333 | 63956.8333 | 81830.8333 | 82690.3333 | 82753.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | 43333.3333 | 34692.6167 | 47368.5417 | 27736.4667 | 20593.0667 | 37512.4667 | 72442
Net cost allocated to water (Air-cooled chiller) | 43333.3333 | 43333.3333 | 39946.2083 | -72171.6667 | -174759.1667 | -179689.6667 | -180046.6667
NVW (Gross Production) | 0 | 0 | 256.9113 | 10.8541 | 7.4396 | 7.3536 | 7.3475
NVW (Net Delivered, No Credit) | 0 | 0 | 491.7915 | 21.3813 | 9.4851 | 8.0956 | 7.9454
Fair NVW (Dry cooler + Air cooled chiller) | 0 | 0 | 530.2634 | 9.2725 | 2.387 | 3.6726 | 6.9554
Fair NVW (Air cooled chiller) | 0 | 0 | 447.1747 | -24.1276 | -20.2565 | -17.592 | -17.2869
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 2920000 | 2920000 | 2882365.2778 | 1636611.1111 | 496750 | 441966.6667 | 438000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 2920000 | 2919711.6667 | 2741233.3333 | 1713613.3333 | 653123.3333 | 410346.6667 | 394200
PUE_uravu | 1.3333 | 1.3333 | 1.329 | 1.1868 | 1.0567 | 1.0505 | 1.05
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.3333 | 1.3333 | 1.3129 | 1.1956 | 1.0746 | 1.0468 | 1.045
WUE | 0 | 0 | -0.010198 | -0.34147 | -0.98485 | -1.166 | -1.189
Grid CO₂ (kg/kWh) | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
Grid water (L/kWh) | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
Uravu water foot print (m3/year) | 6716 | 6716 | 6629.4401 | 3764.2056 | 1142.525 | 1016.5233 | 1007.4
Uravu CO2 emission (tCO₂/yr) | 2190 | 2190 | 2161.774 | 1227.4583 | 372.5625 | 331.475 | 328.5
Cooling tower + Air cooled chiller mixed mode analysis
Variable | Value | Value | Value | Value | Value | Value | Value
Hours Cooling is Sufficient | 0 | 90 | 3915 | 8729 | 8760 | 8760 | 8760
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 309630.7053 | 307416.7323 | 213322.8798 | 94899.924 | 94137.3333 | 94137.3333 | 94137.3333
Fair NVW (Dry cooler + Air cooled chiller) |  |  |  | 43.3135 | 3.215 | 2.2328 | 2.1554
Stand-alonecooling tower + air-cooled chiller power consumption | 2920000 | 2890900 | 1654150 | 97623.3333 | 87600 | 87600 | 87600
PUE_Cooling_tower_chiller | 1.3333 | 1.33 | 1.1888 | 1.0111 | 1.01 | 1.01 | 1.01

## Singapore
------------------------------------------------------------------
Uravu Final strategic & Techno-Economic Evaluation Report for Uravu-waste heat system
------------------------------------------------------------------
--------Input parameters-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Facility water inlet temperature(deg C) | 30 | 35 | 40 | 45 | 50 | 55 | 60
Cooling Requirement (deg C) | 18 | 23 | 28 | 33 | 38 | 43 | 48
Electricity cost ($/kWh) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
CAPEX ($) | 500000 | 500000 | 500000 | 500000 | 500000 | 500000 | 500000
Ammortization period (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Boiling Point elevation (deg C) | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mass flow rate of facility water (kg/s) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
----------------Uravu System Performance & Power-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Max Production (Heat Limited) (kg/hr) | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286 | 80.2286
Rated Power (Normal Operation) (kW) | 4.0935 | 4.0935 | 4.0935 | 4.0935 | 4.0935 | 4.0935 | 4.0935
Rated Power (with Pre-Cooling) (kW) | 4.3435 | 4.3435 | 4.3435 | 4.3435 | 4.3435 | 4.3435 | 4.3435
Uravu electrical consumption (kWh) | 0 | 0 | 8.687 | 11323.5149 | 37762.4238 | 38049.095 | 38049.095
System Downtime Trigger (WBT) (deg C) | 9.5 | 14.5 | 19.5 | 24.5 | 29.5 | 34.5 | 39.5
Vapor Temperature (deg C) | 12.5 | 17.5 | 22.5 | 27.5 | 32.5 | 37.5 | 42.5
Facility water outlet temperature (deg C) | 23.5 | 28.5 | 33.5 | 38.5 | 43.5 | 48.5 | 53.5
Hours evaporative cooler is operational for facility water | 0 | 0 | 0 | 3 | 0 | 0 | 0
Hours chiller is operational for facility water cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total downtime due to WBT trigger | 8760 | 8760 | 8758 | 6089 | 56 | 0 | 0
Total downtine due to high water usage | 0 | 0 | 0 | 64 | 10 | 0 | 0
Annual Downtime Hours (hr) | 8760 | 8760 | 8758 | 6153 | 66 | 0 | 0
Reduction in chiller load (%) | 0 | 0 | 0.022831 | 29.7603 | 99.2466 | 100 | 100
---------------------Annual Water Balance (tonnes/year)-------------------------
Variable | Value | Value | Value | Value | Value | Value | Value
Gross water produced (m³/MW/year) | 0 | 0 | 2.5714 | 3351.8571 | 11178 | 11262.8571 | 11262.8571
water used for pre-cooling in Uravu (m³/MW/year) | 0 | 0 | 1.8257 | 890.6914 | 1699.6886 | 73.8 | 0
Water used for cooling faciltiy water (m³/MW/year) | 0 | 0 | 0 | 0.04898 | 0 | 0 | 0
Net Water Delivered to Customer (m³/MW/year) | 0 | 0 | 0.74571 | 2461.1167 | 9478.3114 | 11189.0571 | 11262.8571
----------------Tier Mixed-Mode Baseline Analysis (The "Avoided Cost")-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Tier 1 (Free Cooling) Trigger:DBT <= | 13 | 18 | 23 | 28 | 33 | 38 | 43
Hours Dry Cooler is Sufficient | 0 | 0 | 92 | 5921 | 8740 | 8760 | 8760
Hours Air-cooled Chiller Required | 8760 | 8760 | 8668 | 2839 | 20 | 0 | 0
Electricity Cost ($) | 584000 | 584000 | 578694.6667 | 242555.6667 | 79993.3333 | 78840 | 78840
Total annualized cost (Uravu + Air cooled chiller ($/MW) | 661166.6667 | 661166.6667 | 661053.3333 | 513436.6667 | 168506.6667 | 164766.6667 | 164766.6667
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 617833.3333 | 617833.3333 | 621194.6667 | 285055.6667 | 122493.3333 | 87506.6667 | 87506.6667
Total avoided cost (Air-cooled chiller($/MW)) | 617833.3333 | 617833.3333 | 617833.3333 | 617833.3333 | 617833.3333 | 617833.3333 | 617833.3333
----------------Final Financials ($/MW) & Levelized Cost of Water ($/m³)-------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Cost | 43333.3333 | 43333.3333 | 43353.3333 | 69403.3333 | 130273.3333 | 130933.3333 | 130933.3333
Net Cost Allocated to Water (Dry cooler + Air cooled chiller) | 43333.3333 | 43333.3333 | 39858.6667 | 228381 | 46013.3333 | 77260 | 77260
Net cost allocated to water (Air-cooled chiller) | 43333.3333 | 43333.3333 | 43220 | -104396.6667 | -449326.6667 | -453066.6667 | -453066.6667
NVW (Gross Production) | 0 | 0 | 16859.6296 | 20.7059 | 11.6544 | 11.6252 | 11.6252
NVW (Net Delivered, No Credit) | 0 | 0 | 58136.6539 | 28.1999 | 13.7444 | 11.7019 | 11.6252
Fair NVW (Dry cooler + Air cooled chiller) | 0 | 0 | 53450.3193 | 92.7957 | 4.8546 | 6.905 | 6.8597
Fair NVW (Air cooled chiller) | 0 | 0 | 57957.8544 | -42.4184 | -47.4058 | -40.4919 | -40.2266
----------------Annual power consumption (kWh), PUE, and WUE (L/kWh)---------------
Variable | Value | Value | Value | Value | Value | Value | Value
Total Annualized Uravu Power consumption | 2920000 | 2920000 | 2919433.3333 | 2181350 | 456700 | 438000 | 438000
Stand-alone air-cooled chiller power consumption | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000 | 2920000
Stand-alone dry cooler + air-cooled chiller power consumption | 2920000 | 2920000 | 2893473.3333 | 1212778.3333 | 399966.6667 | 394200 | 394200
PUE_uravu | 1.3333 | 1.3333 | 1.3333 | 1.249 | 1.0521 | 1.05 | 1.05
PUE_chiller_standalone | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
PUE_dry_cooler_chiller | 1.3333 | 1.3333 | 1.3303 | 1.1384 | 1.0457 | 1.045 | 1.045
WUE | 0 | 0 | -8.5127e-05 | -0.28095 | -1.082 | -1.2773 | -1.2857
Grid CO₂ (kg/kWh) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Grid water (L/kWh) | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
Uravu water foot print (m3/year) | 2336 | 2336 | 2335.5467 | 1745.08 | 365.36 | 350.4 | 350.4
Uravu CO2 emission (tCO₂/yr) | 1168 | 1168 | 1167.7733 | 872.54 | 182.68 | 175.2 | 175.2
Cooling tower + Air cooled chiller mixed mode analysis
Variable | Value | Value | Value | Value | Value | Value | Value
Hours Cooling is Sufficient | 0 | 1 | 1424 | 8652 | 8760 | 8760 | 8760
Total avoided Cost (dry cooler + Air cooled chiller($/MW)) | 630827.4933 | 630768.0773 | 546219.1093 | 116760.2613 | 110343.3333 | 110343.3333 | 110343.3333
Fair NVW (Dry cooler + Air cooled chiller) |  |  |  | 161.1774 | 6.1365 | 4.864 | 4.8321
Stand-alonecooling tower + air-cooled chiller power consumption | 2920000 | 2919676.6667 | 2459573.3333 | 122520 | 87600 | 87600 | 87600
PUE_Cooling_tower_chiller | 1.3333 | 1.3333 | 1.2808 | 1.014 | 1.01 | 1.01 | 1.01