## Slide 1
Cloud Operations & Innovation (“CO+ I”)
A Feasibility Framework for Waste Heat from Data Centers to a Water Capture System from Uravu Labs
Milestone-3 Preliminary Report

## Slide 2: System Configurations
Baseline 1 Air-cooled chiller (ACC)
  No data center waste heat utilization
  Cooling is achieved through air-cooled chiller high power consumption due to low COP values
B Dry cooler (DC) + Air cooled chiller (ACC)
  No data center waste heat utilization
  Cooling is achieved through combination of DC and ACC based on local ambient condition low power consumption than Baseline 1 due to free cooling

## Slide 3: System Configurations
Uravu-waste heat Waste heat is utilized to drive the vapor generation process for the given Uravu uptime.
  Unblended system Chiller cost is not considered
  Blended system Uravu-waste heat + ACC added chiller capex and opex
    For Uravu-uptime In case of further cooling air- cooled chiller (ACC) reduces the chiller load (<< 1 MW)
    For Uravu-downtime Cooling is provided through ACC only chiller load = 1 MW
Uravu-electric
  Waste heat is utilized for partial preheating of the liquid desiccant.
  No Uravu downtime but higher electricity consumption
  Remaining cooling Chiller reduces the chiller load (<< 1 MW).

## Slide 4
Parameters | Value/source | Unit
Project lifetime | 15 | Years
Electricity cost | ~0.1–0.2 (source) | $/kWh
CAPEX (Uravu-waste heat) | ~500,000 | $/MW
CAPEX (Uravu-electric) | ~650,000 | $/MW
CAPEX (Air-cooled chiller) | ~350,000 | $/MW
CAPEX (Dry-cooler) | ~100,000 | $/MW
Maintenance rate (Uravu unit) | ~2 | %
Maintenance rate (Air-cooled chiller) | ~3 | %
Maintenance rate (Dry cooler) | ~2 | %
Power consumption (Uravu-waste heat) | ~50 | kW
Power consumption (Uravu-electric) | ~200 | kW
Power consumption (ACC) | ~333.33 | kW
Power consumption (DC) | ~45 | kW

## Slide 5: Levelized Cost of Cooling (LCOC) - $/MWh
For Madrid at :
Uravu-waste heat + ACC Uravu-electric
At high-temperature waste heat for all cities:
Uravu-waste heat (unblended) << other configurations due to high uptime
European Union

## Slide 6
For Phoenix and Houston at :
Uravu-waste heat + ACC Uravu-electric
At high-temperature waste heat for all cities:
Uravu-waste heat (unblended) << other configurations due to high uptime
United States

## Slide 7: Key takeaways
For regions with high ambient temperature (Madrid, Phoenix and Houston):
  Preferable to use Uravu-electric system at low-temperature waste heat ()
  At waste heat > 35, Uravu-waste heat (unblended) and Uravu-waste heat + ACC system is more suitable options with approximately same LCOC
For colder regions:
  Uravu-waste heat (unblended) and Uravu-waste heat + ACC system is more preferable at all temperatures
DC + ACC system shows lower LCOC due to free cooling but has no waste heat utilization